## READ ME
The minimum daily load (MDL) data posted on the next tab is public information from PGE’s OASIS website under the “Generation Interconnection – Oregon Small Generator Interconnection – Additional Information” folder at the following link: http://www.oatioasis.com/pge/ The Oregon Community Solar Program Administrator has added a new column that calculates the Eligible Capacity (MW) for solar generators applying through the Community Solar Program (CSP) interconnection process. The calculation for CSP interconnection process eligibility on PGE’s feeders is the MDL minus proposed generation. The data is current as of 1/29/2020. Please see PGE's disclaimer on the next tab for more information.

## Sheet1
PGE Distribution System Data | [12 empty] | As of 1/29/2020
DISCLAIMER: This distribution system information provides a high-level system overview and is provided for information purposes only. It is not intended to replace the established interconnection process. This information represents a snapshot of the system and the interconnection queue at the time it was produced, is not updated with every system or queue change, and may not reflect the current system or queue. Project-specific interconnection requirements and costs can be determined only by completing the applicable interconnection process. To obtain the right to interconnect to PGE’s system, a project must complete the applicable interconnection process. PGE shall not be held liable under any circumstances for any errors, omissions, inaccurate, and/or out-of-date content or information provided. By producing this distribution system information, PGE makes no warranty or guarantee about the ability to interconnect or costs to do so. In addition, PGE makes no warranty of merchantability or fitness for any particular purpose and disclaims any and all liability with respect to the accuracy or currency of the information provided, or the fitness or appropriateness of the information for any particular use. This information is supplied with all faults.
Key
Indicates feeders which may require substation upgrades to accommodate additional net metering generation.
Substation Name | Feeder Name | Feeder ID# | Feeder Voltage (kV) | Area | County | SCADA (Y/N) | Transformer position | Transformer rating (MVA) | Peak Load (MVA) | Distribution line rating (MVA) [Note: The conductor is the first feeder section outside the substation. This is not necessarily the smallest conductor in the entire backbone of the feeder.] | DER Capacity Connected (MW) [includes small gen & net metering] | DER Capacity In Queue (MW) [includes small gen only] | Minimum Daytime Load (MW) | CSP Eligible Capacity (MW)
ABERNETHY | ABERNETHY-OREGON CITY | 6105023 | 13 | Oregon City | Clackamas | Y | WR1 | 16.8 | 7.7 | 17.8 | 0.3113 | 0 | 2.1868 | 2.1868
ABERNETHY | ABERNETHY-TRANSIT | 6105033 | 13 | Oregon City | Clackamas | Y | WR1 | 16.8 | 5 | 17.8 | 0.07466 | 0 | 0.99378 | 0.99378
ABERNETHY | ABERNETHY-CLACKAMAS HEIGHTS | 6105013 | 13 | Oregon City | Clackamas | Y | WR2 | 28 | 4.7 | 14.3 | 2.5 | 0 | 0.20532 | 0.20532
ABERNETHY | ABERNETHY-WASHINGTON | 6105043 | 13 | Oregon City | Clackamas | Y | WR2 | 28 | 5.9 | 17.8 | 0.04366 | 0 | 3.115 | 3.115
ALDER | ALDER-ANKENY | 1118013 | 13 | Portland | Multnomah | Y | WR1 | 28 | 5.39 | 17.8 | 0.02782 | 0 | 0.82164 | 0.82164
ALDER | ALDER-LINCOLN | 1118043 | 13 | Portland | Multnomah | Y | WR1 | 28 | 9.6 | 17.8 | 0.51562 | 0 | 3.9858 | 3.9858
ALDER | ALDER-STARK | 1118033 | 13 | Portland | Multnomah | Y | WR1 | 28 | 9.1 | 18.6 | 0.08414 | 0 | 3.8886 | 3.8886
ALDER | ALDER-IRVING | 1118053 | 13 | Portland | Multnomah | Y | WR2 | 28 | 8.7 | 18.6 | 0.10039 | 0 | 3.7897 | 3.7897
ALDER | ALDER-TAYLOR | 1118063 | 13 | Portland | Multnomah | Y | WR2 | 28 | 6.18 | 17.8 | 0.087385 | 0 | 1.8082 | 1.8082
ALDER | ALDER-YAMHILL | 1118073 | 13 | Portland | Multnomah | Y | WR2 | 28 | 2 | 17.8 | 0.043965 | 0 | 0.919 | 0.919
AMITY | AMITY-BELLEVUE | 2120023 | 13 | near Amity | Yamhill | N | BR1 | 7.5 | 4.955 | 7.8 | 1.5316 | 0 | 0.595 | 0.595
AMITY | AMITY-AMITY 13 | 2120013 | 13 | near Amity | Yamhill | N | BR2 | 7.8 | 4.59 | 7.4 | 1.8753 | 0 | 0.44 | 0.44
ARLETA | ARLETA-FOSTER | 1125033 | 13 | Portland | Multnomah | N | BR2 | 25.2 | 4.7 | 9.5 | 0.0686 | 0 | 2.1974 | 2.1974
ARLETA | ARLETA-POWELL | 1125043 | 13 | Portland | Multnomah | N | BR2 | 25.2 | 7 | 10 | 2.6166 | 0 | 2.6586 | 2.6586
ARLETA | ARLETA-STEELE | 1125053 | 13 | Portland | Multnomah | N | BR2 | 25.2 | 8 | 10.3 | 0.3159 | 0 | 2.5806 | 2.5806
ARLETA | ARLETA-52ND | 1125013 | 13 | Portland | Multnomah | N | BR3 | 16.8 | 8.56 | 14.3 | 0.26452 | 0 | 3.0686 | 3.0686
ARLETA | ARLETA-HAROLD | 1125023 | 13 | Portland | Multnomah | N | BR3 | 16.8 | 7.3 | 10 | 0.22886 | 0 | 2.105 | 2.105
BANKS | BANKS-BANKS 13 | 4135013 | 13 | Banks | Washington | Y | BR1 | 20 | 2.44 | 7.3 | 0.18684 | 0 | 0.78025 | 0.78025
BANKS | BANKS-CEDAR CANYON | 4135023 | 13 | Banks | Washington | Y | BR1 | 20 | 8.81 | 17.8 | 0.33101 | 0 | 3.058 | 3.058
BARNES | BARNES-BOONE | 2140013 | 13 | Salem | Marion | N | WR1 | 21.2 | 6.8 | 17.8 | 0.02247 | 0 | 2.565 | 2.565
BARNES | BARNES-COMMERCIAL | 2140023 | 13 | Salem | Marion | N | WR1 | 21.2 | 10 | 17.8 | 0.44896 | 0 | 2.055 | 2.055
BARNES | BARNES-BATTLE CREEK | 2140043 | 13 | Salem | Marion | N | WR2 | 21.2 | 6.8 | 17.8 | 0.21709 | 0 | 0.35 | 0.35
BARNES | BARNES-SUNNYSIDE | 2140033 | 13 | Salem | Marion | N | WR2 | 21.2 | 11.5 | 17.8 | 0.41583 | 0 | 2.195 | 2.195
BEAVERTON | BEAVERTON-JAMIESON | 4150023 | 13 | Beaverton | Washington | Y | WR1 | 16.8 | 8.7 | 17.8 | 0.006 | 0 | 2.8419 | 2.8419
BEAVERTON | BEAVERTON-NORTHWEST | 4150033 | 13 | Beaverton | Washington | Y | WR1 | 16.8 | 3.8 | 17.8 | 0.0608 | 0 | 1.3705 | 1.3705
BEAVERTON | BEAVERTON-ALLEN | 4150013 | 13 | Beaverton | Washington | Y | WR2 | 16.8 | 7.3 | 17.8 | 0.20706 | 0 | 2.3476 | 2.3476
BEAVERTON | BEAVERTON-WEST SLOPE | 4150053 | 13 | Beaverton | Washington | Y | WR2 | 16.8 | 9.5 | 17.8 | 0.3726 | 0 | 3.8544 | 3.8544
BELL | BELL-BRENTWOOD | 1155083 | 13 | Portland | Clackamas | Y | WR1 | 16.8 | 2.64 | 17.8 | 0.01302 | 0 | 1.1456 | 1.1456
BELL | BELL-BATTIN | 1155073 | 13 | Portland | Clackamas | Y | WR2 | 28 | 3.9 | 18.6 | 0.21538 | 0 | 1.8865 | 1.8865
BELL | BELL-FLAVEL | 1155023 | 13 | Portland | Clackamas | Y | WR2 | 28 | 7.9 | 17.8 | 0.14478 | 0 | 1.2493 | 1.2493
BELL | BELL-KENDALL | 1155053 | 13 | Portland | Clackamas | Y | WR2 | 28 | 4.3 | 17.8 | 1.1817 | 0 | 1.2797 | 1.2797
BELL | BELL-KING | 1155063 | 13 | Portland | Clackamas | Y | WR3 | 21 | 8 | 17.8 | 0.20706 | 0 | 2.0856 | 2.0856
BELL | BELL-SOUTHGATE | 1155043 | 13 | Portland | Clackamas | Y | WR3 | 21 | 5.7 | 10.7 | 0.09298 | 0 | 1.9772 | 1.9772
BELL | BELL-WICHITA | 1155033 | 13 | Portland | Clackamas | Y | WR3 | 21 | 6.93 | 10.7 | 0.14403 | 0 | 0.5 | 0.5
BELL | *REDACTED* | 1155013 | 13 | Portland | Clackamas | Y | WR1 | 16.8 | *REDACTED* | 17.8 | 0 | 0 | *REDACTED* | 0
BETHANY | BETHANY-GERMANTOWN | 4157013 | 13 | Portland | Washington | Y | WR1 | 28 | 13.99 | 17.8 | 0.74354 | 0 | 3.2522 | 3.2522
BETHANY | BETHANY-KAISER | 4157023 | 13 | Portland | Washington | Y | WR1 | 28 | 11.31 | 17.8 | 0.51857 | 0 | 2.024 | 2.024
BETHANY | BETHANY-THOMPSON | 4157033 | 13 | Portland | Washington | Y | WR1 | 28 | 3.43 | 17.8 | 0.06267 | 0 | 0.93713 | 0.93713
BETHANY | BETHANY-BURTON | 4157043 | 13 | Portland | Washington | Y | WR2 | 28 | 8.72 | 17.8 | 0.38438 | 0 | 1.5103 | 1.5103
BETHANY | BETHANY-LAIDLAW | 4157053 | 13 | Portland | Washington | Y | WR2 | 28 | 11.78 | 17.8 | 0.73058 | 0 | 1.9687 | 1.9687
BETHANY | BETHANY-SPRINGVILLE | 4157063 | 13 | Portland | Washington | Y | WR2 | 28 | 7.8 | 17.8 | 1.6674 | 0 | 0.54746 | 0.54746
BETHEL | BETHEL-FRUITLAND | 2151023 | 13 | Salem | Marion | Y | WR5 | 28 | 7.1326 | 14.3 | 0.22193 | 0 | 2.2821 | 2.2821
BETHEL | BETHEL-GEER | 2151033 | 13 | Salem | Marion | Y | WR5 | 28 | 6 | 14.3 | 0.3658 | 1.75 | 1.7782 | 0.028207
BETHEL | BETHEL-MACLEAY | 2151013 | 13 | Salem | Marion | Y | WR5 | 28 | 5.6 | 17.8 | 0.095655 | 0 | 1.8263 | 1.8263
BLUE LAKE | BLUE LAKE-BLUE LAKE 13 | 5156013 | 13 | Troutdale | Multnomah | Y | WR1 | 28 | 10.9 | 17.8 | 1.293 | 0 | 3.3608 | 3.3608
BLUE LAKE | BLUE LAKE-SUNDIAL | 5156033 | 13 | Troutdale | Multnomah | Y | WR1 | 28 | 11.2 | 18.4 | 0 | 0 | 3.3054 | 3.3054
BLUE LAKE | BLUE LAKE-TOYO TANSO | 5156023 | 13 | Troutdale | Multnomah | Y | WR1 | 28 | 4.9 | 18.4 | 0.21508 | 0 | 1.2185 | 1.2185
BOONES FERRY | BOONES FERRY-LAKE GROVE | 1170033 | 13 | Lake Oswego | Clackamas | Y | WR1 | 28 | 9.4 | 14.3 | 0.02976 | 0 | 3.0415 | 3.0415
BOONES FERRY | BOONES FERRY-MOUNTAIN PARK | 1170053 | 13 | Lake Oswego | Clackamas | Y | WR1 | 28 | 8.4 | 17.8 | 0.05024 | 0 | 2.2758 | 2.2758
BOONES FERRY | BOONES FERRY-GOODALL | 1170043 | 13 | Lake Oswego | Clackamas | Y | WR2 | 22 | 6 | 10.7 | 0.06208 | 0 | 1.8721 | 1.8721
BOONES FERRY | BOONES FERRY-KRUSE | 1170013 | 13 | Lake Oswego | Clackamas | Y | WR2 | 22 | 9.5 | 17.8 | 0.013785 | 0 | 3.0116 | 3.0116
BOONES FERRY | BOONES FERRY-WEMBLEY PARK | 1170023 | 13 | Lake Oswego | Clackamas | Y | WR2 | 22 | 6.9 | 17.8 | 0.09098 | 0 | 2.1913 | 2.1913
BORING | BORING-TELFORD | 5177013 | 13 | near Boring | Clackamas | Y | BR1 | 7.5 | 6.6 | 14.3 | 0.11807 | 0 | 2.8631 | 2.8631
BORING | BORING-282ND | 5177033 | 13 | near Boring | Clackamas | Y | BR2 | 16.8 | 8.2 | 17.8 | 0.34334 | 0 | 2.763 | 2.763
BORING | BORING-CITY | 5177023 | 13 | near Boring | Clackamas | Y | BR2 | 16.8 | 5.7 | 10.7 | 0.51041 | 5.2604 | 1.6291 | -3.6314
BRIGHTWOOD | BRIGHTWOOD-BRIGHTWOOD 13 | 5174013 | 13 | Sandy | Clackamas | Y | BR1 | 9.4 | 3.7 | 10.4 | 0.042485 | 0 | 0.999 | 0.999
BRIGHTWOOD | BRIGHTWOOD-NORTH BANK | 5174023 | 13 | Sandy | Clackamas | Y | BR1 | 9.4 | 3.1 | 10.7 | 0.01347 | 10 | 0.81017 | -9.1898
BROOKWOOD | BROOKWOOD-BORWICK | 4185023 | 13 | near Hillsboro | Washington | Y | BR1 | 28 | 7.72 | 17.8 | 1.0834 | 0 | 3.0182 | 3.0182
BROOKWOOD | BROOKWOOD-BROOKWOOD 13 | 4185013 | 13 | near Hillsboro | Washington | Y | BR1 | 28 | 9.84 | 18.4 | 0.0278 | 0.175 | 4.5787 | 4.4037
BROOKWOOD | BROOKWOOD-SUNRISE | 4185033 | 13 | near Hillsboro | Washington | Y | BR1 | 28 | 8.87 | 17.8 | 0.23058 | 0 | 4.1833 | 4.1833
CANBY | CANBY-FILBERT | 6190033 | 13 | near Barlow | Clackamas | N | BR1 | 9.4 | 0 | 14.3 | 0 | 0 | 0 | 0
CANBY | CANBY-13644 | 6190023 | 13 | near Barlow | Clackamas | N | BR2 | 14 | 2.4 | 7.3 | 0.04222 | 0 | 0 | 0
CANBY | CANBY-ZIMMERMAN | 6190053 | 13 | near Barlow | Clackamas | N | BR3 | 7.5 | 8.5 | 14.7 | 1.495 | 1.98 | 2.3 | 0.32
CANBY | CANBY-BUTTEVILLE | 6190043 | 13 | near Barlow | Clackamas | N | BR4 | 8.4 | 6.3 | 18.9 | 2.2444 | 0 | 0.735 | 0.735
CANYON | CANYON-13114 NETWORK 1 | 1196113 | 13 | Portland | Multnomah | Y | WR1 | 50 | 2.1 | 7 | 0 | 0 | -0.0052495 | -0.0052495
CANYON | CANYON-13120 | 1196043 | 13 | Portland | Multnomah | Y | WR1 | 50 | 5.3 | 7 | 0.001 | 0 | 2.2 | 2.2
CANYON | CANYON-13122 NETWORK 2 | 1196063 | 13 | Portland | Multnomah | Y | WR1 | 50 | 2.1 | 7.5 | 0 | 0 | -0.0052495 | -0.0052495
CANYON | CANYON-13133 NETWORK 3 | 1196173 | 13 | Portland | Multnomah | Y | WR1 | 50 | 3.3 | 11.2 | 0 | 0 | -0.035408 | -0.035408
CANYON | CANYON-21ST | 1196023 | 13 | Portland | Multnomah | Y | WR1 | 50 | 8.1 | 14.3 | 0.0023 | 0 | -0.0070659 | -0.0070659
CANYON | CANYON-13115 NETWORK 1 | 1196123 | 13 | Portland | Multnomah | Y | WR2 | 50 | 3 | 7 | 0 | 0 | -0.0052495 | -0.0052495
CANYON | CANYON-13119 PSU | 1196163 | 13 | Portland | Multnomah | Y | WR2 | 50 | 3.75 | 7 | 0 | 0 | 1.3265 | 1.3265
CANYON | CANYON-13123 NETWORK 2 | 1196073 | 13 | Portland | Multnomah | Y | WR2 | 50 | 2.7 | 7.5 | 0 | 0 | -0.0052495 | -0.0052495
CANYON | CANYON-13134 NETWORK 3 | 1196183 | 13 | Portland | Multnomah | Y | WR2 | 50 | 5.4 | 11.2 | 0 | 0 | -0.0052495 | -0.0052495
CANYON | CANYON-CANYON 13 | 1196013 | 13 | Portland | Multnomah | Y | WR2 | 50 | 5.13 | 17.8 | 0.0611 | 0 | 1.8595 | 1.8595
CANYON | CANYON-13116 NETWORK 1 | 1196133 | 13 | Portland | Multnomah | Y | WR3 | 50 | 1.96 | 7 | 0 | 0 | -0.0052495 | -0.0052495
CANYON | CANYON-13118 PSU | 1196153 | 13 | Portland | Multnomah | Y | WR3 | 50 | 1.47 | 5.6 | 0.05 | 0 | 0.40896 | 0.40896
CANYON | CANYON-13124 NETWORK 2 | 1196083 | 13 | Portland | Multnomah | Y | WR3 | 50 | 3.2 | 7.5 | 0 | 0 | -0.0052495 | -0.0052495
CANYON | CANYON-13135 NETWORK 3 | 1196193 | 13 | Portland | Multnomah | Y | WR3 | 50 | 4.8 | 11.2 | 0 | 0 | -0.0052495 | -0.0052495
CANYON | CANYON-23RD | 1196103 | 13 | Portland | Multnomah | Y | WR3 | 50 | 8.39 | 17.8 | 0.07344 | 0 | 3.4817 | 3.4817
CANYON | CANYON-13117 NETWORK 1 | 1196143 | 13 | Portland | Multnomah | Y | WR4 | 50 | 2.98 | 7 | 0 | 0 | 0.73453 | 0.73453
CANYON | CANYON-13121 | 1196453 | 13 | Portland | Multnomah | Y | WR4 | 50 | 1.8 | 5.6 | 0 | 0 | 0.50441 | 0.50441
CANYON | CANYON-13125 NETWORK 2 | 1196093 | 13 | Portland | Multnomah | Y | WR4 | 50 | 2.79 | 7.5 | 0 | 0 | 0.76127 | 0.76127
CANYON | CANYON-13136 NETWORK 3 | 1196203 | 13 | Portland | Multnomah | Y | WR4 | 50 | 5.01 | 11.2 | 0 | 0 | 1.3673 | 1.3673
CANYON | CANYON-BURNSIDE | 1196033 | 13 | Portland | Multnomah | Y | WR4 | 50 | 7.4 | 14.3 | 0.001 | 0 | 3.9839 | 3.9839
CARVER | CARVER-ALMOND | 5198033 | 13 | Carver | Clackamas | Y | WR2 | 28 | 8.3 | 17.8 | 0.09582 | 0 | 2.2622 | 2.2622
CARVER | CARVER-CARVER 13 | 5198013 | 13 | Carver | Clackamas | Y | WR2 | 28 | 8.8 | 17.8 | 0.16525 | 0 | 3.7923 | 3.7923
CARVER | CARVER-RIVERBEND | 5198023 | 13 | Carver | Clackamas | Y | WR2 | 28 | 10.9 | 17.8 | 0.49728 | 0 | 1.6108 | 1.6108
CARVER | CARVER-NORTH | 5198053 | 13 | Carver | Clackamas | Y | WR3 | 28 | 10.9 | 17.8 | 0.25059 | 0 | 3.349 | 3.349
CARVER | CARVER-SOUTH | 5198063 | 13 | Carver | Clackamas | Y | WR3 | 28 | 6.5 | 17.8 | 2.0145 | 0 | 1.7749 | 1.7749
CARVER | CARVER-WOODS | 5198043 | 13 | Carver | Clackamas | Y | WR3 | 28 | 11.27 | 17.8 | 0.20034 | 0 | 2.0654 | 2.0654
CEDAR HILLS | CEDAR HILLS-SHOPPING | 4200013 | 13 | near Beaverton | Washington | Y | WR1 | 28 | 7.65 | 17.8 | 0.11391 | 0 | 3.1297 | 3.1297
CEDAR HILLS | CEDAR HILLS-LEAHY | 4200063 | 13 | near Beaverton | Washington | Y | WR2 | 28 | 10.07 | 14.3 | 0.31284 | 0 | 3.1647 | 3.1647
CEDAR HILLS | CEDAR HILLS-SKYLINE | 4200043 | 13 | near Beaverton | Washington | Y | WR2 | 28 | 3.54 | 17.8 | 0.01846 | 0 | 1.5379 | 1.5379
CEDAR HILLS | CEDAR HILLS-SYLVAN | 4200023 | 13 | near Beaverton | Washington | Y | WR2 | 28 | 7.36 | 17.8 | 0.11444 | 0 | 3.1026 | 3.1026
CEDAR HILLS | *REDACTED* | 4200033 | 13 | near Beaverton | Washington | Y | WR1 | 28 | *REDACTED* | 14.3 | 0 | 0 | *REDACTED* | 0
CEDAR HILLS | *REDACTED* | 4200053 | 13 | near Beaverton | Washington | Y | WR1 | 28 | *REDACTED* | 17.8 | 0 | 0 | *REDACTED* | 0
CENTENNIAL | CENTENNIAL-BARKER | 5202053 | 13 | near Gresham | Multnomah | N | WR1 | 22.4 | 8.2 | 14.3 | 0.14338 | 0 | 3.0111 | 3.0111
CENTENNIAL | CENTENNIAL-CENTENNIAL 13 | 5202033 | 13 | near Gresham | Multnomah | N | WR1 | 22.4 | 4.9 | 14.3 | 1.6537 | 0 | 1.2111 | 1.2111
CENTENNIAL | CENTENNIAL-BRAECROFT | 5202043 | 13 | near Gresham | Multnomah | N | WR2 | 16.8 | 10.2 | 17.8 | 0.1385 | 0 | 3.175 | 3.175
CENTENNIAL | CENTENNIAL-TREELAND | 5202063 | 13 | near Gresham | Multnomah | N | WR2 | 16.8 | 8.3 | 14.3 | 0.08724 | 0 | 4.2161 | 4.2161
CLACKAMAS | CLACKAMAS-EVELYN | 6205023 | 13 | Clackamas | Clackamas | Y | WR1 | 15 | 4.8 | 17.8 | 0.01624 | 0 | 1.4663 | 1.4663
CLACKAMAS | CLACKAMAS-GLADSTONE | 6205013 | 13 | Clackamas | Clackamas | Y | WR1 | 15 | 8.3 | 17.8 | 2.097 | 0 | 1.2346 | 1.2346
CLACKAMAS | CLACKAMAS-JENNIFER | 6205033 | 13 | Clackamas | Clackamas | Y | WR2 | 25.5 | 6.25 | 17.8 | 0 | 0 | 1.9901 | 1.9901
CLACKAMAS | CLACKAMAS-TOLBERT | 6205043 | 13 | Clackamas | Clackamas | Y | WR2 | 25.5 | 12.85 | 17.8 | 2.4256 | 0 | 4.7218 | 4.7218
CLAXTAR | CLAXTAR-CLAXTAR 13 | 2207013 | 13 | Salem | Marion | N | BR1 | 28 | 4.1 | 14.3 | 0 | 0 | 2.46 | 2.46
CLAXTAR | CLAXTAR-HAYESVILLE | 2207023 | 13 | Salem | Marion | N | BR1 | 28 | 6.175 | 17.8 | 0.03479 | 0 | 2.1716 | 2.1716
CLAXTAR | CLAXTAR-RIDGE | 2207033 | 13 | Salem | Marion | N | BR1 | 28 | 8 | 17.8 | 0.37518 | 0 | 2.3793 | 2.3793
COFFEE CREEK | COFFEE CREEK-FREEMAN | 4209023 | 13 | Sherwood | Washington | Y | WR1 | 28 | 8.8 | 17.8 | 0 | 0 | 1.7538 | 1.7538
COFFEE CREEK | COFFEE CREEK-HOLIDAY | 4209013 | 13 | Sherwood | Washington | Y | WR1 | 28 | 7.9 | 17.8 | 0 | 0 | 2.1573 | 2.1573
COLTON | COLTON-DHOOGHE | 6208013 | 13 | Colton | Clackamas | Y | BR1 | 7.5 | 3.0052 | 5 | 0.0591 | 0 | -1.4822 | -1.4822
COLTON | COLTON-GRAYS HILL | 6208023 | 13 | Colton | Clackamas | Y | BR1 | 7.5 | 4.5604 | 10.4 | 0.03412 | 0 | 1.4833 | 1.4833
CORNELIUS | CORNELIUS-ADAIR | 4210033 | 13 | Cornelius | Washington | Y | BR1 | 28 | 5.63 | 17.8 | 0.132 | 0 | 2.2961 | 2.2961
CORNELIUS | CORNELIUS-CORNELIUS 13 | 4210013 | 13 | Cornelius | Washington | Y | BR1 | 28 | 9.2 | 14.3 | 0.33885 | 0 | 3.777 | 3.777
CORNELIUS | CORNELIUS-VERBOORT | 4210023 | 13 | Cornelius | Washington | Y | BR1 | 28 | 5.31 | 14.3 | 0.25809 | 2.97 | 2.0211 | -0.94889
CORNELL | CORNELL-BLUFFS | 4206023 | 13 | Portland | Washington | Y | WR1 | 28 | 11.5 | 17.8 | 0.50821 | 0 | 3.0822 | 3.0822
CORNELL | CORNELL-SALTZMAN | 4206013 | 13 | Portland | Washington | Y | WR1 | 28 | 4.72 | 17.8 | 0.021325 | 0 | 1.8346 | 1.8346
CORNELL | CORNELL-WESTLAWN | 4206033 | 13 | Portland | Washington | Y | WR1 | 28 | 9.94 | 17.8 | 0.15115 | 0 | 4.3996 | 4.3996
CULVER | CULVER-CULVER 13 | 2211143 | 13 | Salem | Marion | Y | WR1 | 28 | 0.046309 | 17.8 | 0 | 0 | -0.020453 | -0.020453
CULVER | CULVER-GAFFIN | 2211113 | 13 | Salem | Marion | Y | WR1 | 28 | 1.523 | 17.8 | 0 | 0 | 0.19008 | 0.19008
CULVER | *REDACTED* | 2211123 | 13 | Salem | Marion | Y | WR1 | 28 | *REDACTED* | 24.9 | 0 | 0 | *REDACTED* | 0
CULVER | *REDACTED* | 2211133 | 13 | Salem | Marion | Y | WR1 | 28 | *REDACTED* | 24.9 | 0 | 0 | *REDACTED* | 0
CURTIS | CURTIS-11077 11.1KV | 1212012 | 13 | Portland | Multnomah | Y | WR1 | 16.8 | 2.9 | 8.9 | 0 | 0 | 0.71035 | 0.71035
CURTIS | CURTIS-CURTIS 13 | 1212013 | 13 | Portland | Multnomah | Y | WR1 | 16.8 | 7.36 | 14.3 | 0.07066 | 0 | 0.74596 | 0.74596
DAYTON | DAYTON-EAST | 4220013 | 13 | near Dayton | Yamhill | Y | BR1 | 7.5 | 7.8534 | 17.8 | 0.93034 | 2.2202 | 2.4117 | 0.19151
DAYTON | DAYTON-LAFAYETTE | 4220033 | 13 | near Dayton | Yamhill | Y | BR3 | 14 | 6.5 | 17.8 | 0.54527 | 0 | 2.0824 | 2.0824
DAYTON | DAYTON-SOUTHWEST | 4220023 | 13 | near Dayton | Yamhill | Y | BR3 | 14 | 3 | 17.8 | 0.62532 | 2.2 | -1.4055 | -3.6055
DELAWARE | DELAWARE-DENVER | 1221013 | 13 | Portland | Multnomah | Y | WR2 | 22.4 | 8.9 | 18.4 | 0.30155 | 0 | 3.0157 | 3.0157
DELAWARE | DELAWARE-INTERSTATE | 1221023 | 13 | Portland | Multnomah | Y | WR2 | 22.4 | 5 | 9.9 | 0.066795 | 0 | 1.9759 | 1.9759
DELAWARE | DELAWARE-LOMBARD | 1221033 | 13 | Portland | Multnomah | Y | WR2 | 22.4 | 11.6 | 17.8 | 0.18467 | 0 | 2.6149 | 2.6149
DENNY | DENNY-NORTH | 4222013 | 13 | Beaverton | Washington | Y | WR1 | 28 | 11.6 | 17.8 | 0.1529 | 0 | 3.1172 | 3.1172
DENNY | DENNY-WEST | 4222023 | 13 | Beaverton | Washington | Y | WR1 | 28 | 7.1 | 17.8 | 0.44961 | 0 | 1.296 | 1.296
DENNY | DENNY-EAST | 4222043 | 13 | Beaverton | Washington | Y | WR2 | 28 | 5.8 | 17.8 | 0.14007 | 0 | 1.7504 | 1.7504
DENNY | DENNY-SOUTH | 4222033 | 13 | Beaverton | Washington | Y | WR2 | 28 | 8.4 | 17.8 | 0.18806 | 0 | 2.7885 | 2.7885
DILLEY | DILLEY-DILLEY 13 | 4223013 | 13 | near Forest Grove | Washington | Y | BR1 | 12.5 | 3.92 | 17.8 | 0.10914 | 0 | 1.3421 | 1.3421
DILLEY | *REDACTED* | 4223023 | 13 | near Forest Grove | Washington | Y | BR1 | 12.5 | *REDACTED* | 11 | 0 | 0 | *REDACTED* | 0
DUNNS CORNER | DUNNS CORNER-DUNNS CORNER 13 | 5218013 | 13 | near Sandy | Clackamas | Y | BR1 | 14 | 6.7 | 17.8 | 0.09997 | 6.7457 | 1.0598 | -5.6858
DUNNS CORNER | DUNNS CORNER-KELSO | 5218023 | 13 | near Sandy | Clackamas | Y | BR1 | 14 | 1.8 | 17.8 | 0.058715 | 2.5521 | 0.59157 | -1.9606
DURHAM | DURHAM-DURHAM 13 | 4224013 | 13 | Tigard | Washington | Y | WR3 | 28 | 10.8 | 17.8 | 0.002 | 0 | 2.9691 | 2.9691
DURHAM | DURHAM-SATTLER | 4224023 | 13 | Tigard | Washington | Y | WR3 | 28 | 8 | 17.8 | 0.30828 | 0 | 1.6662 | 1.6662
DURHAM | DURHAM-BONITA | 4224043 | 13 | Tigard | Washington | Y | WR4 | 28 | 9.9 | 17.8 | 0.181 | 0 | 3.2462 | 3.2462
DURHAM | DURHAM-BRIDGEPORT | 4224053 | 13 | Tigard | Washington | Y | WR4 | 28 | 8.1 | 17.8 | 0.18855 | 0 | 2.6121 | 2.6121
DURHAM | DURHAM-SOUTH | 4224033 | 13 | Tigard | Washington | Y | WR4 | 28 | 3.7 | 17.8 | 2.1122 | 0 | 2.7663 | 2.7663
E EAST | E-11021 11.1KV | 1225012 | 11 | Portland | Multnomah | Y | WK1 WK2 WK3 | 62.4 | 0.9 | 16 | 0 | 0 | 0.17411 | 0.17411
E EAST | E-11040 11.1KV | 1225032 | 11 | Portland | Multnomah | Y | WK1 WK2 WK3 | 62.4 | 4.65 | 8.9 | 0.20737 | 0 | 0.91178 | 0.91178
E EAST | E-11041 11.1KV | 1225042 | 11 | Portland | Multnomah | Y | WK1 WK2 WK3 | 62.4 | 4.1 | 16 | 0.189 | 0 | 0.86972 | 0.86972
E EAST | E-11043 11.1KV | 1225062 | 11 | Portland | Multnomah | Y | WK1 WK2 WK3 | 62.4 | 5.4 | 8.9 | 0.1272 | 0 | 1.4546 | 1.4546
E EAST | E-11047 11.1KV | 1225112 | 11 | Portland | Multnomah | Y | WK1 WK2 WK3 | 62.4 | 7.06 | 12.8 | 0.1474 | 0 | 1.6958 | 1.6958
E EAST | E-13141 | 1225033 | 13 | Portland | Multnomah | Y | WR4 WR5 | 70 | 8.68 | 13.9 | 0 | 0 | 3.5334 | 3.5334
E EAST | E-13144 | 1225083 | 13 | Portland | Multnomah | Y | WR4 WR5 | 70 | 7.34 | 17.8 | 0.9196 | 0 | 2.4449 | 2.4449
E EAST | E-13148 | 1225053 | 13 | Portland | Multnomah | Y | WR4 WR5 | 70 | 5.46 | 13.9 | 0.0404 | 0 | 2.3536 | 2.3536
E EAST | E-13150 | 1225073 | 13 | Portland | Multnomah | Y | WR4 WR5 | 70 | 8.41 | 14.3 | 6.7236 | 0 | 0.16568 | 0.16568
E EAST | *REDACTED* | 1225122 | 11 | Portland | Multnomah | Y | WK1 WK2 WK3 | 62.4 | *REDACTED* | 12.8 | 0 | 0 | *REDACTED* | 0
E WEST | E-13139 | 1225013 | 13 | Portland | Multnomah | Y | WR13 WR14 WR15 | 62.4 | 5.4 | 17.8 | 0.00995 | 0 | 2.2268 | 2.2268
E WEST | E-13140 | 1225023 | 13 | Portland | Multnomah | Y | WR13 WR14 WR15 | 62.4 | 7.85 | 17.8 | 0.01811 | 0 | 3.2717 | 3.2717
E WEST | E-13142 | 1225093 | 13 | Portland | Multnomah | Y | WR13 WR14 WR15 | 62.4 | 7.29 | 13.9 | 2.0605 | 0 | 2.5461 | 2.5461
E WEST | E-13145 | 1225043 | 13 | Portland | Multnomah | Y | WR13 WR14 WR15 | 62.4 | 6.09 | 14.3 | 0.0092 | 0 | 2.8674 | 2.8674
E WEST | E-13149 | 1225063 | 13 | Portland | Multnomah | Y | WR13 WR14 WR15 | 62.4 | 8.12 | 13.9 | 0.18948 | 0 | 3.9367 | 3.9367
E WEST | *REDACTED* | 1225022 | 11 | Portland | Multnomah | Y | WK27 | 70 | *REDACTED* | 16 | 0 | 0 | *REDACTED* | 0
E WEST | *REDACTED* | 1225052 | 11 | Portland | Multnomah | Y | WK27 | 70 | *REDACTED* | 9.4 | 0 | 0 | *REDACTED* | 0
EAGLE CREEK | EAGLE CREEK-BARTON | 5230013 | 13 | Eagle Creek | Clackamas | N | BR1 | 14 | 3.5 | 10.4 | 0.052 | 0 | 1.11 | 1.11
EAGLE CREEK | EAGLE CREEK-RIVER MILL | 5230023 | 13 | Eagle Creek | Clackamas | N | BR1 | 14 | 5.9 | 10.7 | 0.28074 | 0 | 1.46 | 1.46
EASTPORT | EASTPORT-76TH | 1231023 | 13 | Portland | Multnomah | Y | WR1 | 16.8 | 7.9 | 10.4 | 0.169 | 0 | 3.2999 | 3.2999
EASTPORT | EASTPORT-PLAZA | 1231013 | 13 | Portland | Multnomah | Y | WR1 | 16.8 | 6.15 | 10.4 | 0.04952 | 0 | 3.0001 | 3.0001
ELMA | ELMA-ELMA 13 | 2233013 | 13 | near Salem | Marion | Y | BR1 | 28 | 3.8267 | 17.8 | 0.06368 | 0 | 1.0268 | 1.0268
ELMA | ELMA-FOUR CORNERS | 2233023 | 13 | near Salem | Marion | Y | BR1 | 28 | 9.1 | 14.3 | 0.13306 | 0 | 3.8018 | 3.8018
ELMA | ELMA-HUDSON | 2233043 | 13 | near Salem | Marion | Y | BR2 | 28 | 10.3 | 14.3 | 0.074195 | 0 | 4.392 | 4.392
ELMA | ELMA-STATE | 2233033 | 13 | near Salem | Marion | Y | BR2 | 28 | 7.2 | 17.8 | 1.9698 | 0 | 3.0302 | 3.0302
ESTACADA | ESTACADA-ESTACADA 13 | 5237023 | 13 | Estacada | Clackamas | Y | BR1 | 14 | 9.5 | 18.4 | 0.209 | 12.565 | 3.3353 | -9.2297
ESTACADA | ESTACADA-NORTH FORK | 5237033 | 13 | Estacada | Clackamas | Y | BR1 | 14 | 6.6 | 17.8 | 0.05 | 0 | 2.2171 | 2.2171
ESTACADA | ESTACADA-FARADAY | 5237013 | 13 | Estacada | Clackamas | Y | BR2 | 15.6 | 8.7 | 17.8 | 0.24631 | 2.2 | 2.1538 | -0.046156
FAIRMOUNT | FAIRMOUNT-CANDALARIA | 2250013 | 13 | Salem | Marion | N | WR1 | 25 | 8.1 | 17.8 | 0.35121 | 0 | 2.7225 | 2.7225
FAIRMOUNT | FAIRMOUNT-MISSION | 2250023 | 13 | Salem | Marion | N | WR1 | 25 | 8.5 | 17.8 | 0.25316 | 0 | 2.7216 | 2.7216
FAIRVIEW | FAIRVIEW-FAIRVIEW 13 | 5251053 | 13 | Fairview | Multnomah | Y | WR1 | 22.4 | 6.5 | 17.8 | 0.04173 | 0 | 1.4673 | 1.4673
FAIRVIEW | FAIRVIEW-TROUTDALE | 5251043 | 13 | Fairview | Multnomah | Y | WR1 | 22.4 | 10.9 | 17.8 | 0.13368 | 0 | 4.1055 | 4.1055
FAIRVIEW | FAIRVIEW-WOOD VILLAGE | 5251023 | 13 | Fairview | Multnomah | Y | WR1 | 22.4 | 8.7 | 17.8 | 0.05481 | 0 | 0.99385 | 0.99385
FAIRVIEW | FAIRVIEW-CLEAR CREEK | 5251033 | 13 | Fairview | Multnomah | Y | WR2 | 22.4 | 2.3 | 18.4 | 0 | 0 | 0.7478 | 0.7478
FAIRVIEW | FAIRVIEW-KENNEL CLUB | 5251013 | 13 | Fairview | Multnomah | Y | WR2 | 22.4 | 11.7 | 17.8 | 0.056145 | 0 | 2.2135 | 2.2135
FARGO | FARGO-FARGO 13 | 2253013 | 13 | Aurora | Marion | N | WR1 | 8.4 | 9.075 | 17.8 | 0.16497 | 2 | 3.17 | 1.17
GALES CREEK | GALES CREEK-GALES CREEK 13 | 4275013 | 13 | Forest Grove | Washington | Y | BR1 | 3 | 3.59 | 7.8 | 0.11779 | 0 | 0.77352 | 0.77352
GARDEN HOME | GARDEN HOME-MCKAY | 4276023 | 13 | near Portland | Washington | Y | WR1 | 21 | 7 | 17.8 | 0.24341 | 0 | 1.395 | 1.395
GARDEN HOME | GARDEN HOME-METZGER | 4276013 | 13 | near Portland | Washington | Y | WR1 | 21 | 9.8 | 17.8 | 0.23361 | 0 | 3.521 | 3.521
GLENCOE | GLENCOE-GLISAN | 1277013 | 13 | Portland | Multnomah | N | WR1 | 25 | 7.12 | 9.9 | 0.33512 | 0 | 2.7571 | 2.7571
GLENCOE | GLENCOE-SUNNYSIDE | 1277033 | 13 | Portland | Multnomah | N | WR1 | 25 | 7.38 | 17.8 | 0.38052 | 0 | 2.4571 | 2.4571
GLENCOE | *REDACTED* | 1277023 | 13 | Portland | Multnomah | N | WR1 | 25 | *REDACTED* | 9.9 | 0 | 0 | *REDACTED* | 0
GLENCULLEN | GLENCULLEN-BRIDLEMILE | 1278013 | 13 | Portland | Multnomah | N | WR1 | 24 | 8.25 | 17.8 | 0.28176 | 0 | 2.6 | 2.6
GLENCULLEN | GLENCULLEN-SUNSET | 1278023 | 13 | Portland | Multnomah | N | WR1 | 24 | 5.4 | 17.8 | 0.20644 | 0 | 1.8623 | 1.8623
GLENDOVEER | GLENDOVEER-13596 | 5280013 | 13 | near Portland | Multnomah | Y | WR2 | 22.4 | 5 | 17.8 | 0.01788 | 0 | 2.0698 | 2.0698
GLENDOVEER | GLENDOVEER-13597 | 5280023 | 13 | near Portland | Multnomah | Y | WR2 | 22.4 | 4.6 | 17.8 | 0.04483 | 0 | 1.8465 | 1.8465
GLENDOVEER | GLENDOVEER-13599 | 5280043 | 13 | near Portland | Multnomah | Y | WR2 | 22.4 | 5.5 | 17.8 | 0.080445 | 0 | 1.8953 | 1.8953
GLENDOVEER | GLENDOVEER-13598 | 5280033 | 13 | near Portland | Multnomah | Y | WR4 | 28 | 5.6 | 17.8 | 0.1376 | 0 | 1.4123 | 1.4123
GLENDOVEER | GLENDOVEER-CLIFGATE | 5280053 | 13 | near Portland | Multnomah | Y | WR4 | 28 | 7.8 | 17.8 | 0.134 | 0 | 2.5623 | 2.5623
GLENDOVEER | GLENDOVEER-NORTHEAST | 5280063 | 13 | near Portland | Multnomah | Y | WR4 | 28 | 4.6 | 17.8 | 0.053725 | 0 | 1.4337 | 1.4337
*REDACTED* | *REDACTED* | 5260013 | 13 | Gresham | Multnomah | Y | WR1 | 16.8 | *REDACTED* | 18.4 | 0 | 0 | *REDACTED* | 0
*REDACTED* | *REDACTED* | 5260043 | 13 | Gresham | Multnomah | Y | WR1 | 16.8 | *REDACTED* | 11 | 0 | 0 | *REDACTED* | 0
*REDACTED* | *REDACTED* | 5260033 | 13 | Gresham | Multnomah | Y | WR1 | 16.8 | *REDACTED* | 18.4 | 0 | 0 | *REDACTED* | 0
*REDACTED* | *REDACTED* | 5260023 | 13 | Gresham | Multnomah | Y | WR1 | 16.8 | *REDACTED* | 18.4 | 0 | 0 | *REDACTED* | 0
*REDACTED* | *REDACTED* | 5260063 | 13 | Gresham | Multnomah | Y | WR2 | 28 | *REDACTED* | 18.4 | 0 | 0 | *REDACTED* | 0
*REDACTED* | *REDACTED* | 5260083 | 13 | Gresham | Multnomah | Y | WR2 | 28 | *REDACTED* | 18.4 | 0 | 0 | *REDACTED* | 0
*REDACTED* | *REDACTED* | 5260073 | 13 | Gresham | Multnomah | Y | WR2 | 28 | *REDACTED* | 18.4 | 0 | 0 | *REDACTED* | 0
GRAND RONDE | GRAND RONDE-AGENCY | 2285033 | 13 | Grand Ronde | Polk | Y | WR2 | 12.5 | 1.9839 | 7.8 | 0.14904 | 0 | 0.75075 | 0.75075
GRAND RONDE | GRAND RONDE-FORTHILL | 2285023 | 13 | Grand Ronde | Polk | Y | WR2 | 12.5 | 4.9405 | 10.4 | 2.2176 | 6.6604 | 1.3291 | -5.3314
HARBORTON | HARBORTON-BURLINGTON | 1310023 | 13 | near Portland | Multnomah | Y | WR3 | 25 | 4.8 | 10.4 | 0.18067 | 0 | 1.3968 | 1.3968
HARBORTON | HARBORTON-HARBORTON 13 | 1310013 | 13 | near Portland | Multnomah | Y | WR3 | 25 | 1.41 | 13.7 | 0 | 0 | 0 | 0
HARBORTON | HARBORTON-LINNTON | 1310033 | 13 | near Portland | Multnomah | Y | WR3 | 25 | 3.67 | 10.4 | 0.00712 | 0 | 1.2537 | 1.2537
HARMONY | HARMONY-HARMONY 13 | 1313013 | 13 | near Milwaukie | Clackamas | Y | WR1 | 28 | 8.7 | 17.8 | 0.122 | 0 | 3.9737 | 3.9737
HARMONY | HARMONY-LAKE | 6313033 | 13 | near Milwaukie | Clackamas | Y | WR1 | 28 | 9.9 | 17.8 | 0.64314 | 0 | 3.7621 | 3.7621
HARMONY | HARMONY-MILWAUKIE | 1313023 | 13 | near Milwaukie | Clackamas | Y | WR1 | 28 | 6.49 | 14.3 | 0.16704 | 0 | 1.6412 | 1.6412
HARMONY | HARMONY-INTERNATIONAL | 1313053 | 13 | near Milwaukie | Clackamas | Y | WR2 | 21 | 6.9 | 17.8 | 0.088165 | 0 | 2.2364 | 2.2364
HARMONY | HARMONY-LINWOOD | 1313033 | 13 | near Milwaukie | Clackamas | Y | WR2 | 21 | 6.1 | 14.3 | 0.29057 | 0 | 2.4614 | 2.4614
HARMONY | HARMONY-THIESSEN | 1313043 | 13 | near Milwaukie | Clackamas | Y | WR2 | 21 | 7.96 | 17.8 | 0.05786 | 0 | 2.817 | 2.817
HARRISON | HARRISON-DAVIS | 1312043 | 13 | Portland | Multnomah | Y | WR1 | 28 | 11.5 | 14.3 | 0.50123 | 0 | 5.6964 | 5.6964
HARRISON | HARRISON-HARRISON 13 | 1312053 | 13 | Portland | Multnomah | Y | WR1 | 28 | 9.4 | 17.8 | 0.14512 | 0.0012 | 3.0394 | 3.0382
HARRISON | HARRISON-IVON | 1312013 | 13 | Portland | Multnomah | Y | WR1 | 28 | 7 | 9.5 | 0.05813 | 0 | 3.8125 | 3.8125
HAYDEN ISLAND | HAYDEN ISLAND-MAINLAND | 1316033 | 13 | near Portland | Multnomah | Y | WR1 | 16.8 | 7.2 | 17.8 | 0 | 0 | 1.2515 | 1.2515
HAYDEN ISLAND | HAYDEN ISLAND-SOUTH SHORE | 1316023 | 13 | near Portland | Multnomah | Y | WR1 | 16.8 | 3.02 | 14.3 | 0.29821 | 0 | 1.4048 | 1.4048
HAYDEN ISLAND | HAYDEN ISLAND-NORTH SHORE | 1316013 | 13 | near Portland | Multnomah | Y | WR2 | 16.8 | 7.4 | 14.3 | 0.04035 | 0 | 3.0249 | 3.0249
HEMLOCK | HEMLOCK-FREMONT | 5317023 | 13 | Portland | Multnomah | Y | WR1 | 28 | 4.3 | 17.8 | 0.041985 | 0 | 1.1708 | 1.1708
HEMLOCK | HEMLOCK-HEMLOCK 13 | 5317013 | 13 | Portland | Multnomah | Y | WR1 | 28 | 11.6 | 17.8 | 0.00315 | 0 | 4.5149 | 4.5149
HEMLOCK | HEMLOCK-MASON | 5317033 | 13 | Portland | Multnomah | Y | WR1 | 28 | 11.7 | 17.8 | 1.4345 | 0 | 1.975 | 1.975
HILLCREST | HILLCREST-CASCADIA | 2318033 | 13 | Salem | Marion | Y | WR1 | 28 | 0.6 | 24.9 | 0 | 0 | 0.1017 | 0.1017
HILLCREST | HILLCREST-HILLCREST 13 | 2318023 | 13 | Salem | Marion | Y | WR1 | 28 | 5.5 | 11 | 0.07449 | 0 | 1.2977 | 1.2977
HILLCREST | HILLCREST-REED | 2318043 | 13 | Salem | Marion | Y | WR1 | 28 | 0.11192 | 17.8 | 0.08 | 0 | -0.070412 | -0.070412
HILLCREST | HILLCREST-SOUTH | 2318223 | 13 | Salem | Marion | Y | WR1 | 28 | 6.2 | 18.4 | 0.05625 | 0 | 0.98321 | 0.98321
HILLSBORO | HILLSBORO-JACKSON | 4320033 | 13 | Hillsboro | Washington | Y | BR1 | 21 | 9.75 | 14.3 | 0.53709 | 0 | 3.0894 | 3.0894
HILLSBORO | HILLSBORO-LAUREL | 4320023 | 13 | Hillsboro | Washington | Y | BR1 | 21 | 9.12 | 14.3 | 2.1099 | 0 | 2.8494 | 2.8494
HILLSBORO | HILLSBORO-DAIRY CREEK | 4320013 | 13 | Hillsboro | Washington | Y | BR2 | 22.4 | 13.29 | 17.8 | 2.3999 | 0 | 3.4974 | 3.4974
HILLSBORO | HILLSBORO-DENNIS | 4320053 | 13 | Hillsboro | Washington | Y | BR2 | 22.4 | 2.8 | 17.8 | 0.106 | 0 | 1.1047 | 1.1047
HILLSBORO | HILLSBORO-SCHOLLS | 4320043 | 13 | Hillsboro | Washington | Y | BR2 | 22.4 | 7.84 | 17.8 | 0.08326 | 0 | 2.5851 | 2.5851
HOGAN NORTH | HOGAN NORTH-HOGAN NORTH 13 | 5323043 | 13 | Gresham | Multnomah | Y | WR1 | 28 | 9.3 | 17.8 | 0.14995 | 0 | 3.5958 | 3.5958
HOGAN NORTH | HOGAN NORTH-LINKS | 5323033 | 13 | Gresham | Multnomah | Y | WR1 | 28 | 11 | 17.8 | 0.15678 | 0 | 2.1066 | 2.1066
HOGAN NORTH | HOGAN NORTH-BRIGADOON | 5323023 | 13 | Gresham | Multnomah | Y | WR2 | 28 | 8.8 | 17.8 | 0.10425 | 0 | 3.9688 | 3.9688
HOGAN NORTH | HOGAN NORTH-SALQUIST | 5323013 | 13 | Gresham | Multnomah | Y | WR2 | 28 | 9.4 | 14.3 | 0.12268 | 0 | 3.3147 | 3.3147
HOGAN SOUTH | HOGAN SOUTH-CLEVELAND | 5324013 | 13 | Gresham | Multnomah | Y | WR4 | 28 | 10 | 14.3 | 0.14911 | 0 | 3.7439 | 3.7439
HOGAN SOUTH | HOGAN SOUTH-MAIN | 5324033 | 13 | Gresham | Multnomah | Y | WR4 | 28 | 8.2 | 17.8 | 0.02468 | 0 | 2.5469 | 2.5469
HOGAN SOUTH | HOGAN SOUTH-WALLULA | 5324053 | 13 | Gresham | Multnomah | Y | WR4 | 28 | 7.4 | 14.3 | 0.06348 | 0 | 2.2091 | 2.2091
HOGAN SOUTH | HOGAN SOUTH-LAWRENCE | 5324023 | 13 | Gresham | Multnomah | Y | WR5 | 28 | 11.8 | 17.8 | 0.28902 | 0 | 1.5731 | 1.5731
HOGAN SOUTH | HOGAN SOUTH-PAROPA | 5324043 | 13 | Gresham | Multnomah | Y | WR5 | 28 | 11.3 | 14.3 | 0.21616 | 0 | 3.9817 | 3.9817
HOLGATE | HOLGATE-GIDEON | 1325013 | 13 | Portland | Multnomah | N | BR4 | 16.8 | 3.85 | 14.3 | 0.59998 | 0 | 1.63 | 1.63
HOLGATE | HOLGATE-HOLGATE 13 | 1325033 | 13 | Portland | Multnomah | N | BR4 | 16.8 | 7.8 | 14.3 | 0.31114 | 0 | 3.3714 | 3.3714
HOLGATE | HOLGATE-BYBEE | 1325043 | 13 | Portland | Multnomah | N | BR5 | 22.4 | 8.29 | 14.3 | 0.43224 | 0 | 3.6343 | 3.6343
HOLGATE | HOLGATE-KENILWORTH | 1325053 | 13 | Portland | Multnomah | N | BR5 | 22.4 | 2.8 | 14.3 | 0.096815 | 0 | 1.095 | 1.095
HOLGATE | HOLGATE-RHONE | 1325023 | 13 | Portland | Multnomah | N | BR5 | 22.4 | 6.49 | 14.3 | 0.14648 | 0 | 0.88 | 0.88
HUBER | HUBER-BANY | 4330053 | 13 | near Beaverton | Washington | Y | WR1 | 28 | 13.3 | 17.8 | 0.289 | 0 | 2.9483 | 2.9483
HUBER | HUBER-MARYVILLE | 4330043 | 13 | near Beaverton | Washington | Y | WR1 | 28 | 13.7 | 17.8 | 0.36394 | 0 | 1.4105 | 1.4105
HUBER | HUBER-FARMINGTON | 4330023 | 13 | near Beaverton | Washington | Y | WR2 | 28 | 10.8 | 14.3 | 0.30985 | 0 | 3.9764 | 3.9764
HUBER | HUBER-HUBER 13 | 4330013 | 13 | near Beaverton | Washington | Y | WR2 | 28 | 9.3 | 17.8 | 0.23549 | 0 | 1.1884 | 1.1884
HUBER | HUBER-KINNAMAN | 4330033 | 13 | near Beaverton | Washington | Y | WR2 | 28 | 7.1 | 14.3 | 0.16861 | 0 | 2.3794 | 2.3794
INDIAN | INDIAN-LABISH | 2340013 | 13 | near Salem | Marion | Y | WR1 | 28 | 8.2 | 17.8 | 0.339 | 0 | 2.4477 | 2.4477
INDIAN | INDIAN-WEST | 2340053 | 13 | near Salem | Marion | Y | WR1 | 28 | 12.1 | 17.8 | 0.13084 | 0 | 3.7488 | 3.7488
INDIAN | INDIAN-KEIZER | 2340023 | 13 | near Salem | Marion | Y | WR2 | 28 | 7.1 | 17.8 | 0.1301 | 0 | -0.010599 | -0.010599
INDIAN | INDIAN-NORTH | 2340043 | 13 | near Salem | Marion | Y | WR2 | 28 | 12.8 | 17.8 | 3.224 | 0 | 0.64735 | 0.64735
INDIAN | INDIAN-STATION | 2340033 | 13 | near Salem | Marion | Y | WR2 | 28 | 7.5 | 18.4 | 0.12103 | 0 | 2.6401 | 2.6401
ISLAND | ISLAND-13180 | 1345033 | 13 | near Milwaukie | Clackamas | Y | WR1 | 16.8 | 8.66 | 17.8 | 2.2539 | 0 | 2.7608 | 2.7608
ISLAND | ISLAND-ISLAND 13 | 1345043 | 13 | near Milwaukie | Clackamas | Y | WR1 | 16.8 | 6 | 10.4 | 0.01744 | 0 | 2.7922 | 2.7922
ISLAND | ISLAND-13187 | 1345023 | 13 | near Milwaukie | Clackamas | Y | WR2 | 28 | 9.11 | 17.8 | 0.12162 | 0 | 2.8937 | 2.8937
ISLAND | ISLAND-13188 | 1345013 | 13 | near Milwaukie | Clackamas | Y | WR2 | 28 | 10.5 | 17.8 | 0.12761 | 0 | 4.3597 | 4.3597
JENNINGS LODGE | JENNINGS LODGE-ADDIE | 6365053 | 13 | Jennings Lodge | Clackamas | N | WR1 | 24.5 | 6.42 | 17.8 | 0.043255 | 0 | 1.8086 | 1.8086
JENNINGS LODGE | JENNINGS LODGE-JENNINGS 13 | 6365023 | 13 | Jennings Lodge | Clackamas | N | WR1 | 24.5 | 9.13 | 14.3 | 0.4475 | 0 | 3.1943 | 3.1943
JENNINGS LODGE | JENNINGS LODGE-MELDRUM | 6365033 | 13 | Jennings Lodge | Clackamas | N | WR1 | 24.5 | 6.35 | 10.7 | 0.03956 | 0 | 2.72 | 2.72
JENNINGS LODGE | JENNINGS LODGE-OAK GROVE | 6365013 | 13 | Jennings Lodge | Clackamas | N | WR2 | 28 | 4.5 | 10.7 | 0.07274 | 0 | 1.4857 | 1.4857
JENNINGS LODGE | JENNINGS LODGE-WEBSTER | 6365043 | 13 | Jennings Lodge | Clackamas | N | WR2 | 28 | 7.4 | 14.3 | 0.13478 | 0 | 1.8914 | 1.8914
KELLEY POINT | KELLEY POINT-KELLEY POINT 13 | 1367013 | 13 | Portland | Multnomah | Y | WR1 | 28 | 5.6 | 18.4 | 0 | 0 | 0.21525 | 0.21525
KELLEY POINT | KELLEY POINT-LEDBETTER | 1367043 | 13 | Portland | Multnomah | Y | WR1 | 28 | 2.96 | 18.4 | 0 | 0 | 0.73021 | 0.73021
KELLEY POINT | KELLEY POINT-MARINE | 1367023 | 13 | Portland | Multnomah | Y | WR2 | 28 | 5.1 | 11.01 | 0.06633 | 0 | 1.3495 | 1.3495
KELLEY POINT | KELLEY POINT-SIMMONS | 1367033 | 13 | Portland | Multnomah | Y | WR2 | 28 | 2.46 | 18.4 | 0 | 0 | 0.7364 | 0.7364
KELLEY POINT | *REDACTED* | 1367053 | 13 | Portland | Multnomah | Y | WR1 | 28 | *REDACTED* | 20.9 | 0 | 0 | *REDACTED* | 0
KELLEY POINT | *REDACTED* | 1367063 | 13 | Portland | Multnomah | Y | WR2 | 28 | *REDACTED* | 20.9 | 0 | 0 | *REDACTED* | 0
KELLY BUTTE | KELLY BUTTE-BINNSMEAD | 1370023 | 13 | Portland | Multnomah | Y | WR1 | 22.4 | 9.5 | 17.8 | 0.23992 | 0 | 4.2362 | 4.2362
KELLY BUTTE | KELLY BUTTE-MALL 205 | 1370043 | 13 | Portland | Multnomah | Y | WR1 | 22.4 | 8.4 | 17.8 | 0.10673 | 0 | 2.8295 | 2.8295
KELLY BUTTE | KELLY BUTTE-FAIRLAWN | 1370033 | 13 | Portland | Multnomah | Y | WR2 | 22.4 | 8.8 | 17.8 | 0.25333 | 0 | 4.3371 | 4.3371
KELLY BUTTE | KELLY BUTTE-MCGREW | 1370013 | 13 | Portland | Multnomah | Y | WR2 | 22.4 | 8.7 | 17.8 | 0.2327 | 0 | 3.4643 | 3.4643
KING CITY | KING CITY-BULL MOUNTAIN | 4378023 | 13 | near King City | Washington | N | WR1 | 22 | 9.5 | 17.8 | 0.296 | 0 | 1.506 | 1.506
KING CITY | KING CITY-FISCHER | 4378013 | 13 | near King City | Washington | N | WR1 | 22 | 12.8 | 17.8 | 0.404 | 0 | 2.425 | 2.425
KING CITY | KING CITY-HAZELBROOK | 4378043 | 13 | near King City | Washington | N | WR2 | 28 | 6.5 | 17.8 | 0.095 | 0 | 3.2804 | 3.2804
KING CITY | KING CITY-NORTH | 4378053 | 13 | near King City | Washington | N | WR2 | 28 | 6 | 14.3 | 0.183 | 0 | 2.6931 | 2.6931
KING CITY | KING CITY-SUMMERFIELD | 4378033 | 13 | near King City | Washington | N | WR2 | 28 | 6.9 | 14.3 | 0.073 | 0 | 2.5063 | 2.5063
LELAND | LELAND-BEAVERCREEK | 6402013 | 13 | Oregon City | Clackamas | Y | BR1 | 28 | 10.6 | 17.8 | 0.39753 | 0 | 4.8592 | 4.8592
LELAND | LELAND-CARUS | 6402023 | 13 | Oregon City | Clackamas | Y | BR1 | 28 | 10.65 | 17.8 | 0.39736 | 2.5 | 2.4604 | -0.039596
LELAND | LELAND-KELM | 6402033 | 13 | Oregon City | Clackamas | Y | BR1 | 28 | 8 | 17.8 | 0.21875 | 0 | 2.1513 | 2.1513
LENTS | LENTS-MT SCOTT | 1405023 | 13 | near Portland | Multnomah | Y | BK1 | 10 | 0.8 | 17.8 | 0.02287 | 0 | 0.075715 | 0.075715
LENTS | LENTS-NORTH | 1405033 | 13 | near Portland | Multnomah | Y | RK2 | 10 | 4.2 | 10.4 | 0.07253 | 0 | 1.537 | 1.537
LENTS | LENTS-13101 | 1405013 | 13 | near Portland | Multnomah | Y | WR3 | 22.4 | 6.4 | 17.8 | 0.10191 | 0 | 0.51578 | 0.51578
LENTS | LENTS-HAPPY VALLEY | 1405043 | 13 | near Portland | Multnomah | Y | WR3 | 22.4 | 11.5 | 17.8 | 0.089815 | 0 | 4.2081 | 4.2081
LIBERAL | LIBERAL-LIBERAL 13 | 6464013 | 13 | Molalla | Clackamas | Y | BR1 | 8.4 | 4.7 | 17.8 | 0.21094 | 4.2 | 1.6121 | -2.5879
LIBERAL | *REDACTED* | 6464023 | 13 | Molalla | Clackamas | Y | BR1 | 8.4 | *REDACTED* | 17.8 | 0 | 0 | *REDACTED* | 0
LIBERTY | LIBERTY-BROWNING | 2410013 | 13 | Salem | Marion | Y | WR1 | 22.4 | 2 | 7.8 | 0.01702 | 0 | 0.49586 | 0.49586
LIBERTY | LIBERTY-ROSEDALE | 2410023 | 13 | Salem | Marion | Y | WR1 | 22.4 | 7.6 | 17.8 | 0.46646 | 0 | 2.6236 | 2.6236
LIBERTY | LIBERTY-VISTA | 2410033 | 13 | Salem | Marion | Y | WR1 | 22.4 | 4.9238 | 14.3 | 0.05338 | 0 | 2.022 | 2.022
LIBERTY | LIBERTY-LONE OAK | 2410043 | 13 | Salem | Marion | Y | WR2 | 28 | 7.6 | 17.8 | 0.19414 | 0 | 2.2195 | 2.2195
LIBERTY | LIBERTY-MORNINGSIDE | 2410053 | 13 | Salem | Marion | Y | WR2 | 28 | 7.6 | 14.3 | 0.093875 | 0 | 3.4 | 3.4
LIBERTY | LIBERTY-SKYLINE | 2410063 | 13 | Salem | Marion | Y | WR2 | 28 | 10.5 | 17.8 | 0.39029 | 0 | 4.4595 | 4.4595
MAIN | MAIN-AIRPORT | 4422023 | 13 | Hillsboro | Washington | Y | BR1 | 28 | 5.78 | 17.8 | 0.1653 | 0 | 2.1118 | 2.1118
MAIN | MAIN-BENTLEY | 4422033 | 13 | Hillsboro | Washington | Y | BR1 | 28 | 7.07 | 17.8 | 0.2705 | 0 | 1.8185 | 1.8185
MAIN | MAIN-EXPRESS | 4422053 | 13 | Hillsboro | Washington | Y | BR1 | 28 | 10.23 | 17.8 | 0.092315 | 0 | 4.5699 | 4.5699
MAIN | MAIN-RIVER | 4422013 | 13 | Hillsboro | Washington | Y | BR2 | 28 | 10.2 | 17.8 | 0.40166 | 0 | 3.7076 | 3.7076
MAIN | *REDACTED* | 4422073 | 13 | Hillsboro | Washington | Y | BR2 | 28 | *REDACTED* | 17.8 | 0 | 0 | *REDACTED* | 0
MAIN | *REDACTED* | 4422063 | 13 | Hillsboro | Washington | Y | BR3 | 28 | *REDACTED* | 18.6 | 0 | 0 | *REDACTED* | 0
MAIN | *REDACTED* | 4422043 | 13 | Hillsboro | Washington | Y | BR3 | 28 | *REDACTED* | 18.6 | 0 | 0 | *REDACTED* | 0
MARKET | MARKET-ENGLEWOOD | 2425013 | 13 | Salem | Marion | Y | WR1 | 28 | 7 | 17.8 | 0.0709 | 0 | 1.2809 | 1.2809
MARKET | MARKET-FAIRGROUNDS | 2425033 | 13 | Salem | Marion | Y | WR1 | 28 | 6.0459 | 11 | 0.09351 | 0 | 2.6788 | 2.6788
MARKET | MARKET-HAWTHORNE | 2425023 | 13 | Salem | Marion | Y | WR1 | 28 | 6.4 | 17.8 | 0.00314 | 0 | 2.6625 | 2.6625
MARKET | MARKET-PARK | 2425043 | 13 | Salem | Marion | Y | WR1 | 28 | 4.1 | 17.8 | 4.021 | 0 | -1.0935 | -1.0935
MCCLAIN | MCCLAIN-COTTAGE | 2435033 | 13 | Salem | Marion | Y | BR1 | 7.5 | 3.888 | 14.3 | 0.03531 | 0 | 1.5178 | 1.5178
MCCLAIN | MCCLAIN-HOLLYWOOD | 2435043 | 13 | Salem | Marion | Y | BR2 | 7.5 | 3.8009 | 9.9 | 0.15813 | 0 | 1.6496 | 1.6496
MCCLAIN | MCCLAIN-FRONT | 2435013 | 13 | Salem | Marion | Y | BR3 | 7.5 | 5.5 | 9.9 | 0.06104 | 0 | 1.7668 | 1.7668
*REDACTED* | *REDACTED* | 5440023 | 13 | Gresham | Multnomah | Y | WR1 | 19.4 | *REDACTED* | 11 | 0 | 0 | *REDACTED* | 0
*REDACTED* | *REDACTED* | 5440013 | 13 | Gresham | Multnomah | Y | WR1 | 19.4 | *REDACTED* | 24.9 | 0 | 0 | *REDACTED* | 0
*REDACTED* | *REDACTED* | 5440073 | 13 | Gresham | Multnomah | Y | WR2 | 28 | *REDACTED* | 11 | 0 | 0 | *REDACTED* | 0
*REDACTED* | *REDACTED* | 5440063 | 13 | Gresham | Multnomah | Y | WR2 | 28 | *REDACTED* | 24.9 | 0 | 0 | *REDACTED* | 0
MERIDIAN | MERIDIAN-LAKEVIEW | 4447063 | 13 | near Tualatin | Clackamas | Y | WR1 | 28 | 5.1 | 17.8 | 0.09976 | 0 | 1.8702 | 1.8702
MERIDIAN | MERIDIAN-MERIDIAN 13 | 4447013 | 13 | near Tualatin | Clackamas | Y | WR1 | 28 | 6.3 | 14.3 | 0.14431 | 0 | 1.8903 | 1.8903
MERIDIAN | MERIDIAN-SAGERT | 4447033 | 13 | near Tualatin | Clackamas | Y | WR1 | 28 | 9 | 17.8 | 0.06203 | 0 | 3.9373 | 3.9373
MERIDIAN | MERIDIAN-65TH | 4447083 | 13 | near Tualatin | Clackamas | Y | WR2 | 28 | 4 | 14.3 | 0 | 0 | 1.1697 | 1.1697
MERIDIAN | MERIDIAN-BORLAND | 4447053 | 13 | near Tualatin | Clackamas | Y | WR2 | 28 | 6.3 | 17.8 | 0.15782 | 0 | 0.57723 | 0.57723
MERIDIAN | MERIDIAN-PILKINGTON | 4447043 | 13 | near Tualatin | Clackamas | Y | WR2 | 28 | 8.3 | 17.8 | 0.12865 | 0 | 2.7844 | 2.7844
MERIDIAN | MERIDIAN-CHILDS | 4447093 | 13 | near Tualatin | Clackamas | Y | WR3 | 28 | 7.1 | 14.3 | 0.2614 | 0 | 2.7912 | 2.7912
MERIDIAN | MERIDIAN-NYBERG | 4447073 | 13 | near Tualatin | Clackamas | Y | WR3 | 28 | 3.5 | 17.8 | 0 | 0 | 1.1194 | 1.1194
MIDDLE GROVE | MIDDLE GROVE-BROWN | 2450023 | 13 | near Middle Grove | Marion | Y | WR1 | 22.4 | 8 | 17.8 | 0.206 | 0 | 3.1234 | 3.1234
MIDDLE GROVE | MIDDLE GROVE-SWEGLE | 2450013 | 13 | near Middle Grove | Marion | Y | WR1 | 22.4 | 8 | 14.3 | 2.2671 | 0 | 3.7734 | 3.7734
MIDDLE GROVE | MIDDLE GROVE-CHEMEKETA | 2450043 | 13 | near Middle Grove | Marion | Y | WR2 | 28 | 4.6 | 10.4 | 0.23664 | 0 | 1.4708 | 1.4708
MIDDLE GROVE | MIDDLE GROVE-CORDON | 2450033 | 13 | near Middle Grove | Marion | Y | WR2 | 28 | 11.1 | 17.8 | 0.288 | 4.2 | 3.5359 | -0.6641
MIDDLE GROVE | MIDDLE GROVE-WEST | 2450053 | 13 | near Middle Grove | Marion | Y | WR2 | 28 | 9.6265 | 17.8 | 0.090515 | 0 | 4.1881 | 4.1881
MIDWAY | MIDWAY-DIVISION | 5455013 | 13 | near Portland | Multnomah | N | WR1 | 16.8 | 6.8 | 17.8 | 0.0676 | 0 | 2.5086 | 2.5086
MIDWAY | MIDWAY-DOUGLAS | 5455023 | 13 | near Portland | Multnomah | N | WR1 | 16.8 | 6.7 | 17.8 | 0.063735 | 0 | 2.425 | 2.425
MIDWAY | MIDWAY-LYNCH | 5455033 | 13 | near Portland | Multnomah | N | WR2 | 16.8 | 6 | 17.8 | 0.04482 | 0 | 2.0914 | 2.0914
MIDWAY | MIDWAY-POWELLHURST | 5455043 | 13 | near Portland | Multnomah | N | WR2 | 16.8 | 7.4 | 10.4 | 0.068085 | 0 | 1.63 | 1.63
MILL CREEK | MILL CREEK-EASTLAND | 2540013 | 13 | near Salem | Marion | Y | WR1 | 16.8 | 5.9252 | 10.7 | 0.32826 | 1.26 | 2.0429 | 0.78292
MILL CREEK | MILL CREEK-KUEBLER | 2540023 | 13 | near Salem | Marion | Y | WR1 | 16.8 | 6.3 | 17.8 | 0.10507 | 0 | 2.1554 | 2.1554
MILL CREEK | MILL CREEK-MILL CREEK 13 | 2540033 | 13 | near Salem | Marion | Y | WR1 | 16.8 | 3.7 | 17.8 | 0.01278 | 0 | 1.3097 | 1.3097
MOLALLA | MOLALLA-FOREST | 6466043 | 13 | Molalla | Clackamas | Y | BR1 | 22.4 | 11.1723 | 17.8 | 0.15143 | 1.256 | 1.7719 | 0.51594
MOLALLA | MOLALLA-YODER | 6466033 | 13 | Molalla | Clackamas | Y | BR1 | 22.4 | 9.8 | 14.3 | 0.65719 | 2.97 | 3.5686 | 0.59865
MOLALLA | MOLALLA-BUCKAROO | 6466023 | 13 | Molalla | Clackamas | Y | BR2 | 20 | 9.3 | 14.3 | 0.18081 | 0 | 3.5439 | 3.5439
MOLALLA | MOLALLA-MARQUAM | 6466013 | 13 | Molalla | Clackamas | Y | BR2 | 20 | 5.8695 | 7.3 | 0.23193 | 14.6515 | 0.2606 | -14.3909
MT ANGEL | MT ANGEL-EAST | 2470013 | 13 | Mt. Angel | Marion | Y | BR1 | 20 | 2.7644 | 10.7 | 0.06025 | 0 | 1.101 | 1.101
MT ANGEL | MT ANGEL-WEST | 2470023 | 13 | Mt. Angel | Marion | Y | BR1 | 20 | 8.4 | 10.4 | 1.0888 | 5.17 | 2.0711 | -3.0989
MT PLEASANT | MT PLEASANT-CLAIRMONT | 6475023 | 13 | Oregon City | Clackamas | N | WR1 | 28 | 12.2 | 17.8 | 0.39377 | 0 | 4.0114 | 4.0114
MT PLEASANT | MT PLEASANT-MT VIEW | 6475043 | 13 | Oregon City | Clackamas | N | WR1 | 28 | 9.8 | 17.8 | 0.22785 | 0 | 4.2629 | 4.2629
MT PLEASANT | MT PLEASANT-RIVERCREST | 6475053 | 13 | Oregon City | Clackamas | N | WR2 | 16.8 | 7.3 | 17.8 | 0.0757 | 0 | 1.0514 | 1.0514
MT PLEASANT | MT PLEASANT-SOUTH END | 6475033 | 13 | Oregon City | Clackamas | N | WR2 | 16.8 | 11.5 | 17.8 | 0.33047 | 0 | 2.8486 | 2.8486
MULINO | MULINO-NORTH | 6478013 | 13 | Mulino | Clackamas | N | BR1 | 7.5 | 2.14 | 17.8 | 0.03414 | 0 | 0.80034 | 0.80034
MULINO | MULINO-SOUTH | 6478023 | 13 | Mulino | Clackamas | N | BR1 | 7.5 | 3.8 | 17.8 | 0.14086 | 0 | 1.161 | 1.161
MULTNOMAH | MULTNOMAH-13177 | 1480033 | 13 | Portland | Multnomah | N | WR1 | 22.4 | 9.46 | 17.8 | 0.15323 | 0 | 3.2543 | 3.2543
MULTNOMAH | MULTNOMAH-MULTNOMAH 13 | 1480063 | 13 | Portland | Multnomah | N | WR1 | 22.4 | 6.9 | 17.8 | 0.30496 | 0 | 2.165 | 2.165
MULTNOMAH | MULTNOMAH-13176 | 1480023 | 13 | Portland | Multnomah | N | WR2 | 16.8 | 7.61 | 17.8 | 0.14413 | 0 | 2.8314 | 2.8314
MULTNOMAH | MULTNOMAH-13181 | 1480013 | 13 | Portland | Multnomah | N | WR2 | 16.8 | 5.26 | 17.8 | 0.20901 | 0 | 1.825 | 1.825
MURRAYHILL | MURRAYHILL-MURRAYHILL 13 | 4482013 | 13 | Beaverton | Washington | Y | WR1 | 28 | 12.7 | 17.8 | 0.18912 | 0 | 3.6731 | 3.6731
MURRAYHILL | MURRAYHILL-TEAL | 4482023 | 13 | Beaverton | Washington | Y | WR1 | 28 | 12 | 18.4 | 0.60838 | 0 | 3.3265 | 3.3265
MURRAYHILL | MURRAYHILL-KINTON | 4482033 | 13 | Beaverton | Washington | Y | WR2 | 28 | 13.3 | 17.8 | 2.4389 | 0 | 3.863 | 3.863
MURRAYHILL | MURRAYHILL-REUSSER | 4482043 | 13 | Beaverton | Washington | Y | WR2 | 28 | 8.9 | 18.4 | 2.3291 | 0 | 1.6713 | 1.6713
NEWBERG | NEWBERG-CHEHALEM | 4485033 | 13 | Newberg | Yamhill | Y | WR1 | 22.4 | 9.3676 | 17.8 | 0.71912 | 0 | 2.9255 | 2.9255
NEWBERG | NEWBERG-DUNDEE | 4485023 | 13 | Newberg | Yamhill | Y | WR1 | 22.4 | 9.6 | 17.8 | 0.61818 | 2.5 | 3.6 | 1.1
NEWBERG | NEWBERG-HOOVER PARK | 4485053 | 13 | Newberg | Yamhill | Y | WR2 | 22.4 | 10 | 17.8 | 0.11102 | 0 | 3.6184 | 3.6184
NEWBERG | NEWBERG-NORTH COLLEGE | 4485043 | 13 | Newberg | Yamhill | Y | WR2 | 22.4 | 11 | 17.8 | 0.45309 | 0 | 2.233 | 2.233
NORTH MARION | NORTH MARION-CROSBY | 2505043 | 13 | near Woodburn | Marion | Y | BR1 | 14 | 9.4 | 17.8 | 0.17948 | 0 | 2.7376 | 2.7376
NORTH MARION | NORTH MARION-HUBBARD | 2505013 | 13 | near Woodburn | Marion | Y | BR1 | 14 | 5.7 | 17.8 | 0.18969 | 0 | 1.9866 | 1.9866
NORTH MARION | NORTH MARION-FRONT | 2505033 | 13 | near Woodburn | Marion | Y | BR2 | 7.5 | 4.9 | 10.7 | 0.0996 | 0 | 1.4933 | 1.4933
NORTH MARION | NORTH MARION-MCLAREN | 2505023 | 13 | near Woodburn | Marion | Y | BR3 | 9.4 | 6.8589 | 17.8 | 0.08697 | 0 | 1.5257 | 1.5257
NORTH PLAINS | NORTH PLAINS-MASON HILL | 4510023 | 13 | North Plains | Washington | Y | BR1 | 20 | 8.39 | 10.4 | 1.4777 | 0 | 2.7284 | 2.7284
NORTH PLAINS | NORTH PLAINS-NORTH PLAINS 13 | 4510013 | 13 | North Plains | Washington | Y | BR1 | 20 | 4.91 | 10.4 | 0.12695 | 0 | 1.9388 | 1.9388
NORTHERN | NORTHERN-11009 11.4KV | 1495032 | 11 | Portland | Multnomah | N | BK2 | 13.3 | 5.62 | 12.2 | 0.30511 | 0 | 2.0851 | 2.0851
NORTHERN | NORTHERN-11016 11.1KV | 1495042 | 11 | Portland | Multnomah | N | BK5 | 15 | 0.835 | 8.9 | 0.0053 | 0 | 0.30833 | 0.30833
NORTHERN | NORTHERN-11071 11.4KV | 1495062 | 11 | Portland | Multnomah | N | BK5 | 15 | 4.59 | 9.4 | 0.08147 | 0 | 1.7519 | 1.7519
OAK HILLS | OAK HILLS-FIVE OAKS | 4516033 | 13 | near Beaverton | Washington | Y | WR1 | 28 | 11.9 | 17.8 | 0.21393 | 0 | 5.6362 | 5.6362
OAK HILLS | OAK HILLS-OAK HILLS 13 | 4516013 | 13 | near Beaverton | Washington | Y | WR1 | 28 | 6.4 | 17.8 | 0.24733 | 0 | 1.4972 | 1.4972
OAK HILLS | OAK HILLS-GREENBRIER | 4516053 | 13 | near Beaverton | Washington | Y | WR2 | 28 | 10.4 | 17.8 | 0.14312 | 0 | 3.6405 | 3.6405
OAK HILLS | OAK HILLS-SOMERSET | 4516023 | 13 | near Beaverton | Washington | Y | WR2 | 28 | 4.2 | 17.8 | 0.17076 | 0 | 1.0305 | 1.0305
OAK HILLS | OAK HILLS-WALKER | 4516043 | 13 | near Beaverton | Washington | Y | WR2 | 28 | 7.6 | 17.8 | 0.50153 | 0 | 2.3935 | 2.3935
ORENCO | ORENCO-BASELINE | 4518013 | 13 | near Hillsboro | Washington | Y | WR3 | 25.2 | 14.01 | 17.8 | 0.8303 | 0 | 1.7111 | 1.7111
ORENCO | ORENCO-ORENCO 13 | 4518033 | 13 | near Hillsboro | Washington | Y | WR3 | 25.2 | 6.32 | 17.8 | 0.23379 | 0 | 2.5633 | 2.5633
ORENCO | ORENCO-AMBERGLEN | 4518043 | 13 | near Hillsboro | Washington | Y | WR4 | 28 | 8.42 | 17.8 | 0.068605 | 0 | 3.614 | 3.614
ORENCO | ORENCO-PRIMATE | 4518023 | 13 | near Hillsboro | Washington | Y | WR4 | 28 | 10.09 | 17.8 | 0.30177 | 0 | 3.7153 | 3.7153
ORENCO | ORENCO-231ST | 4518053 | 13 | near Hillsboro | Washington | Y | WR5 | 28 | 10.7 | 17.8 | 0.015045 | 0 | 5.5594 | 5.5594
ORENCO | ORENCO-WILKINS | 4518063 | 13 | near Hillsboro | Washington | Y | WR5 | 28 | 10.51 | 18.4 | 0.13997 | 0 | 5.1984 | 5.1984
ORIENT | ORIENT-BARLOW | 5517023 | 13 | near Gresham | Multnomah | Y | BR1 | 28 | 5.7 | 10.4 | 0.086965 | 0 | 1.71 | 1.71
ORIENT | ORIENT-ORIENT 13 | 5517013 | 13 | near Gresham | Multnomah | Y | BR1 | 28 | 4.2 | 10.4 | 0.44083 | 0 | 1.3249 | 1.3249
ORIENT | ORIENT-OXBOW | 5517033 | 13 | near Gresham | Multnomah | Y | BR1 | 28 | 2.9 | 10.4 | 0.11931 | 0 | 1.0474 | 1.0474
OSWEGO | OSWEGO-MARYLHURST | 1520033 | 13 | Lake Oswego | Clackamas | Y | WR1 | 16.8 | 10.2 | 17.8 | 0.10949 | 0 | 1.7855 | 1.7855
OSWEGO | OSWEGO-PALATINE | 1520043 | 13 | Lake Oswego | Clackamas | Y | WR1 | 16.8 | 6.7 | 10.4 | 0.06814 | 0 | 2.4922 | 2.4922
OSWEGO | OSWEGO-IRON MOUNTAIN | 1520013 | 13 | Lake Oswego | Clackamas | Y | WR3 | 16.8 | 5.7 | 9.9 | 0.022725 | 0 | 2.3926 | 2.3926
OSWEGO | OSWEGO-STAFFORD | 1520023 | 13 | Lake Oswego | Clackamas | Y | WR3 | 16.8 | 5.7 | 17.8 | 0.55985 | 0 | 2.0493 | 2.0493
OXFORD | OXFORD-LEE | 2523063 | 13 | Salem | Marion | Y | WR1 | 22.4 | 6.3 | 17.8 | 8.0342 | 0 | -3.8442 | -3.8442
OXFORD | OXFORD-RURAL | 2523053 | 13 | Salem | Marion | Y | WR1 | 22.4 | 3.6 | 14.3 | 4.204 | 0 | -1.5766 | -1.5766
OXFORD | OXFORD-SHELTON | 2523023 | 13 | Salem | Marion | Y | WR1 | 22.4 | 2.8 | 10.4 | 0.02934 | 0 | 1.4702 | 1.4702
OXFORD | OXFORD-FAIRVIEW | 2523013 | 13 | Salem | Marion | Y | WR2 | 28 | 10 | 17.8 | 0.1855 | 0 | 3.7012 | 3.7012
OXFORD | OXFORD-MADRONA | 2523033 | 13 | Salem | Marion | Y | WR2 | 28 | 3.7 | 14.3 | 0.01 | 0 | 0.92114 | 0.92114
OXFORD | OXFORD-OXFORD 13 | 2523043 | 13 | Salem | Marion | Y | WR2 | 28 | 3.1499 | 17.8 | 0.06758 | 0 | 1.2307 | 1.2307
PENINSULA PARK | PENINSULA PARK-OCKLEY GREEN | 1545021 | 13 | Portland | Multnomah | Y | WR1 | 28 | 5.8 | 17.8 | 0.12575 | 0 | 1.8063 | 1.8063
PORTSMOUTH | *REDACTED* | 1558053 | 13 | Portland | Multnomah | Y | WR1 | 28 | *REDACTED* | 14.3 | 0 | 0 | *REDACTED* | 0
PLEASANT VALLEY | PLEASANT VALLEY-BAXTER | 5553023 | 13 | near Portland | Clackamas | Y | WR1 | 28 | 8.6 | 14.3 | 0.25889 | 0 | 1.6667 | 1.6667
PLEASANT VALLEY | PLEASANT VALLEY-PLEASANT 13 | 5553013 | 13 | near Portland | Clackamas | Y | WR1 | 28 | 6.2 | 14.3 | 0.2119 | 0 | 1.9328 | 1.9328
PLEASANT VALLEY | PLEASANT VALLEY-CLATSOP | 5553053 | 13 | near Portland | Clackamas | Y | WR2 | 28 | 8.4 | 17.8 | 0.59174 | 0 | 1.6475 | 1.6475
PLEASANT VALLEY | PLEASANT VALLEY-MOON | 5553033 | 13 | near Portland | Clackamas | Y | WR2 | 28 | 10.5 | 14.3 | 0.22029 | 0 | 1.641 | 1.641
PLEASANT VALLEY | PLEASANT VALLEY-SUN | 5553043 | 13 | near Portland | Clackamas | Y | WR2 | 28 | 10.4 | 14.3 | 0.24104 | 0 | 3.4219 | 3.4219
PORTSMOUTH | PORTSMOUTH-CARBIDE | 1558013 | 13 | Portland | Multnomah | Y | WR1 | 28 | 10.6 | 17.8 | 0.29093 | 0 | 3.5679 | 3.5679
PORTSMOUTH | PORTSMOUTH-WILLIS | 1558033 | 13 | Portland | Multnomah | Y | WR1 | 28 | 7.3 | 14.3 | 1.8403 | 0 | 2.1675 | 2.1675
REEDVILLE | *REDACTED* | 4583043 | 13 | near Beaverton | Washington | Y | WR2 | 28 | *REDACTED* | 18.4 | 0 | 0 | *REDACTED* | 0
PROGRESS | PROGRESS-HALL | 4565063 | 13 | near Tigard | Washington | Y | WR1 | 22 | 8.2 | 17.8 | 0 | 0 | 3.6835 | 3.6835
PROGRESS | PROGRESS-SAWYER | 4565023 | 13 | near Tigard | Washington | Y | WR1 | 22 | 6.2 | 17.8 | 0.01249 | 0 | 2.0505 | 2.0505
PROGRESS | PROGRESS-WASHINGTON SQ1 | 4565033 | 13 | near Tigard | Washington | Y | WR1 | 22 | 4.7 | 11 | 0 | 0 | 0 | 0
PROGRESS | PROGRESS-GREENBURG | 4565053 | 13 | near Tigard | Washington | Y | WR2 | 28 | 11.2 | 17.8 | 0.15672 | 0 | 3.3231 | 3.3231
PROGRESS | PROGRESS-ROBINSON | 4565013 | 13 | near Tigard | Washington | Y | WR2 | 28 | 6.5 | 17.8 | 0.064845 | 0 | 2.7686 | 2.7686
PROGRESS | PROGRESS-WASHINGTON SQ2 | 4565043 | 13 | near Tigard | Washington | Y | WR2 | 28 | 1.5 | 11 | 0 | 0 | 0.54746 | 0.54746
RALEIGH HILLS | RALEIGH HILLS-DOGWOOD | 4570073 | 13 | near Portland | Washington | Y | WR1 | 28 | 8 | 17.8 | 0.09501 | 0 | 2.3736 | 2.3736
RALEIGH HILLS | RALEIGH HILLS-MONTCLAIR | 4570053 | 13 | near Portland | Washington | Y | WR1 | 28 | 5.6 | 17.8 | 0.070725 | 0 | 1.8039 | 1.8039
RALEIGH HILLS | RALEIGH HILLS-OLESON | 4570063 | 13 | near Portland | Washington | Y | WR1 | 28 | 6.9 | 17.8 | 0.09926 | 0 | 2.5579 | 2.5579
RAMAPO | RAMAPO-EMERALD | 5575023 | 13 | near Portland | Multnomah | Y | WR1 | 28 | 7.7 | 17.8 | 0.14164 | 0 | 2.1087 | 2.1087
RAMAPO | RAMAPO-GILBERT | 5575013 | 13 | near Portland | Multnomah | Y | WR1 | 28 | 5.9 | 17.8 | 0.11741 | 0 | 1.9985 | 1.9985
RAMAPO | RAMAPO-RAMAPO 13 | 5575033 | 13 | near Portland | Multnomah | Y | WR1 | 28 | 10.5 | 17.8 | 0.23135 | 0 | 3.8327 | 3.8327
REDLAND | REDLAND-HENRICI | 6581023 | 13 | near Oregon City | Multnomah | N | WR1 | 22.4 | 7 | 17.8 | 0.19146 | 0 | 2.275 | 2.275
REDLAND | REDLAND-REDLAND 13 | 6581013 | 13 | near Oregon City | Multnomah | N | WR1 | 22.4 | 11.5 | 14.3 | 0.27883 | 2.79 | 3.06 | 0.27
REEDVILLE | REEDVILLE-BLANTON | 4583033 | 13 | near Beaverton | Washington | Y | WR1 | 28 | 8.54 | 17.8 | 0.21954 | 0 | 2.8396 | 2.8396
REEDVILLE | REEDVILLE-HAZELDALE | 4583013 | 13 | near Beaverton | Washington | Y | WR1 | 28 | 8.95 | 17.8 | 0.16392 | 0 | 2.2523 | 2.2523
REEDVILLE | REEDVILLE-TV HIGHWAY | 4583023 | 13 | near Beaverton | Washington | Y | WR1 | 28 | 7.08 | 17.8 | 0.286 | 0 | 1.8384 | 1.8384
REEDVILLE | REEDVILLE-AUGUSTA | 4583083 | 13 | near Beaverton | Washington | Y | WR2 | 28 | 11.15 | 17.8 | 0.5739 | 0 | 3.1256 | 3.1256
REEDVILLE | *REDACTED* | 4583073 | 13 | near Beaverton | Washington | Y | WR2 | 28 | *REDACTED* | 18.4 | 0 | 0 | *REDACTED* | 0
REEDVILLE | *REDACTED* | 4583053 | 13 | near Beaverton | Washington | Y | WR3 | 28 | *REDACTED* | 18.4 | 0 | 0 | *REDACTED* | 0
REEDVILLE | *REDACTED* | 4583063 | 13 | near Beaverton | Washington | Y | WR3 | 28 | *REDACTED* | 18.4 | 0 | 0 | *REDACTED* | 0
REEDVILLE | *REDACTED* | 4583093 | 13 | near Beaverton | Washington | Y | WR3 | 28 | *REDACTED* | 18.4 | 0 | 0 | *REDACTED* | 0
ROCKWOOD | *REDACTED* | 5602063 | 13 | near Gresham | Multnomah | Y | WR3 | 28 | *REDACTED* | 18.4 | 0 | 0 | *REDACTED* | 0
RIVERGATE SOUTH | RIVERGATE SOUTH-11010 11.4KV | 1598012 | 11 | near Portland | Multnomah | Y | WK2 | 22.4 | 3.9 | 11 | 0 | 0 | 0.41381 | 0.41381
RIVERGATE SOUTH | RIVERGATE SOUTH-11011 11.4KV | 1598022 | 11 | near Portland | Multnomah | Y | WK2 | 22.4 | 5.7 | 13 | 0.096195 | 0 | 2.4874 | 2.4874
RIVERGATE SOUTH | RIVERGATE SOUTH-PEARCY | 1598023 | 13 | near Portland | Multnomah | Y | WR3 | 22.4 | 8.68 | 17.8 | 0 | 0 | 1.1599 | 1.1599
*REDACTED* | *REDACTED* | 4679284 | 34.5 | Hillsboro | Washington | Y | WJ1 | 50 | *REDACTED* | 19 | 0 | 0 | *REDACTED* | 0
RIVERVIEW | RIVERVIEW-FULTON | 1600033 | 13 | Portland | Multnomah | Y | WR1 | 28 | 7.45 | 17.8 | 0.38599 | 0 | 3.0606 | 3.0606
RIVERVIEW | RIVERVIEW-MACADAM | 1600023 | 13 | Portland | Multnomah | Y | WR1 | 28 | 5.12 | 17.8 | 0.1486 | 0 | 2.6458 | 2.6458
RIVERVIEW | RIVERVIEW-TERWILLIGER | 1600013 | 13 | Portland | Multnomah | Y | WR1 | 28 | 5.19 | 17.8 | 0.20829 | 0 | 2.2322 | 2.2322
ROCKWOOD | ROCKWOOD-INDUSTRIAL | 5602023 | 13 | near Gresham | Multnomah | Y | WR1 | 28 | 9.1 | 18.4 | 0.0846 | 0 | 2.4436 | 2.4436
ROCKWOOD | ROCKWOOD-ROCKWOOD 13 | 5602013 | 13 | near Gresham | Multnomah | Y | WR1 | 28 | 9.9 | 17.8 | 0.04971 | 0 | 3.6721 | 3.6721
ROCKWOOD | ROCKWOOD-AIRPORT | 5602053 | 13 | near Gresham | Multnomah | Y | WR2 | 22.4 | 3.8 | 18.4 | 6.9 | 0 | -3.4102 | -3.4102
ROCKWOOD | ROCKWOOD-REYNOLDS | 5602033 | 13 | near Gresham | Multnomah | Y | WR2 | 22.4 | 8.4 | 14.3 | 0.3422 | 0 | 3.1772 | 3.1772
ROCKWOOD | ROCKWOOD-WILKES | 5602043 | 13 | near Gresham | Multnomah | Y | WR2 | 22.4 | 4.1 | 22.6 | 0 | 0 | 0.73421 | 0.73421
*REDACTED* | *REDACTED* | 4660024 | 34.5 | Hillsboro | Washington | Y | WJ1 | 50 | *REDACTED* | 19 | 0 | 0 | *REDACTED* | 0
ROSEMONT | ROSEMONT-HIDDEN SPRINGS | 4604123 | 13 | near Lake Oswego | Clackamas | Y | WR1 | 28 | 8.7 | 17.8 | 0.23341 | 0 | 1.6796 | 1.6796
ROSEMONT | ROSEMONT-MOSSY BRAE | 4604113 | 13 | near Lake Oswego | Clackamas | Y | WR1 | 28 | 3.9 | 17.8 | 0.04741 | 0 | 1.1926 | 1.1926
ROSEMONT | ROSEMONT-OVERLOOK | 4604133 | 13 | near Lake Oswego | Clackamas | Y | WR1 | 28 | 12.8 | 17.8 | 0.03101 | 0 | 2.5515 | 2.5515
ROSEWAY | ROSEWAY-ALEXANDER | 4605033 | 13 | Hillsboro | Washington | Y | WR1 | 28 | 8.44 | 17.8 | 0.706 | 0 | 3.0661 | 3.0661
ROSEWAY | ROSEWAY-ESPLANADE | 4605023 | 13 | Hillsboro | Washington | Y | WR1 | 28 | 7.82 | 17.8 | 0.00713 | 0 | 3.2825 | 3.2825
ROSEWAY | ROSEWAY-ROSEWAY 13 | 4605013 | 13 | Hillsboro | Washington | Y | WR1 | 28 | 7.44 | 17.8 | 0.214 | 0 | 2.5835 | 2.5835
RUBY | RUBY-CARLINE | 5620113 | 13 | Gresham | Multnomah | Y | WR1 | 28 | 9.1 | 17.8 | 0.29186 | 0 | 3.373 | 3.373
RUBY | RUBY-JUNCTION | 5620123 | 13 | Gresham | Multnomah | Y | WR1 | 28 | 9.4 | 17.8 | 0.17239 | 0 | 4.168 | 4.168
SALEM | SALEM-13260 | 2637013 | 13 | near Salem | Marion | Y | BR1 | 22.4 | 4.1 | 10.4 | 0 | 0 | 0.79587 | 0.79587
SALEM | SALEM-13263 | 2637043 | 13 | near Salem | Marion | Y | BR1 | 22.4 | 3.6 | 10.4 | 0.02928 | 0 | 1.0687 | 1.0687
SALEM | SALEM-UNION | 2637053 | 13 | near Salem | Marion | Y | BR1 | 22.4 | 4 | 13.9 | 0.02938 | 0 | 1.0903 | 1.0903
SALEM | SALEM-13261 | 2637023 | 13 | near Salem | Marion | Y | BR2 | 22.4 | 2.7 | 12.6 | 0.099 | 0 | 1.0739 | 1.0739
SALEM | SALEM-13262 | 2637033 | 13 | near Salem | Marion | Y | BR2 | 22.4 | 5 | 12.6 | 0.0255 | 0 | 2.1315 | 2.1315
SALEM | SALEM-13264 | 2637063 | 13 | near Salem | Marion | Y | BR2 | 22.4 | 2.5 | 12.6 | 1.5 | 0 | 0.17963 | 0.17963
SANDY | SANDY-362ND | 5640043 | 13 | Sandy | Clackamas | Y | BR1 | 28 | 8 | 10.7 | 0.03817 | 0 | 3.1739 | 3.1739
SANDY | SANDY-BLUFF | 5640013 | 13 | Sandy | Clackamas | Y | BR1 | 28 | 4.1 | 17.8 | 1.4635 | 0 | 0.5636 | 0.5636
SANDY | SANDY-SANDY 13 | 5640033 | 13 | Sandy | Clackamas | Y | BR1 | 28 | 8.2 | 17.8 | 0.13423 | 14.545 | 3.4227 | -11.1223
SANDY | SANDY-WILDCAT | 5640023 | 13 | Sandy | Clackamas | Y | BR1 | 28 | 8.5 | 10.4 | 0.18768 | 1.85 | 3.588 | 1.738
SCHOLLS FERRY | SCHOLLS FERRY-KEMMER | 4645113 | 13 | Beaverton | Washington | Y | WR1 | 28 | 3.5 | 17.8 | 0.07994 | 0 | 0.85656 | 0.85656
SCHOLLS FERRY | SCHOLLS FERRY-RAINBOW | 4645123 | 13 | Beaverton | Washington | Y | WR1 | 28 | 5.9 | 14.3 | 0.43468 | 0 | 1.4328 | 1.4328
SCHOLLS FERRY | SCHOLLS FERRY-ROY ROGERS | 4645133 | 13 | Beaverton | Washington | Y | WR1 | 28 | 6 | 14.3 | 0.61149 | 0 | 2.1951 | 2.1951
SCOGGINS | SCOGGINS-CHERRY GROVE | 4650023 | 13 | near Gaston | Washington | Y | BR1 | 3.6 | 2.2 | 7.4 | 0.08117 | 0 | 0.54643 | 0.54643
SCOGGINS | SCOGGINS-LAURELWOOD | 4650013 | 13 | near Gaston | Washington | Y | BR2 | 9.4 | 5.6 | 7.4 | 2.386 | 0 | -0.17139 | -0.17139
SCOTTS MILLS | SCOTTS MILLS-SCOTTS MILLS 13 | 2652013 | 13 | Scotts Mills | Marion | N | BR1 | 9.4 | 7.655 | 17.8 | 0.20024 | 2 | 1.575 | -0.425
SELLWOOD | SELLWOOD-KELLOGG PARK | 1655013 | 13 | Portland | Multnomah | Y | WR2 | 28 | 5.89 | 17.8 | 0.18861 | 0 | 2.5653 | 2.5653
SELLWOOD | SELLWOOD-SELLWOOD 13 | 1655033 | 13 | Portland | Multnomah | Y | WR2 | 28 | 12.2 | 16.8 | 0.25847 | 0 | 4.8191 | 4.8191
SELLWOOD | SELLWOOD-WAVERLY | 1655023 | 13 | Portland | Multnomah | Y | WR2 | 28 | 8.67 | 17.8 | 0.31171 | 0 | 2.488 | 2.488
SHERIDAN | SHERIDAN-EAST | 2660023 | 13 | Sheridan | Yamhill | Y | BR1 | 16.8 | 5.8241 | 17.8 | 0.13108 | 3 | 0.73772 | -2.2623
SHERIDAN | SHERIDAN-KADELL | 2660013 | 13 | Sheridan | Yamhill | Y | BR1 | 16.8 | 6.0118 | 17.8 | 2.2624 | 12.2 | 0.28343 | -11.9166
*REDACTED* | *REDACTED* | 4660014 | 34.5 | Hillsboro | Washington | Y | WJ1 | 50 | *REDACTED* | 19 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679114 | 34.5 | near Hillsboro | Washington | Y | WJ9 | 125 | *REDACTED* | 50 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679124 | 34.5 | near Hillsboro | Washington | Y | WJ9 | 125 | *REDACTED* | 50 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679234 | 34.5 | near Hillsboro | Washington | Y | WJ10 | 125 | *REDACTED* | 50 | 0 | 0 | *REDACTED* | 0
SILVERTON | SILVERTON-SOUTH | 2665023 | 13 | Silverton | Marion | Y | BR1 | 14 | 9.1 | 17.8 | 0.2594 | 0 | 2.9318 | 2.9318
SILVERTON | SILVERTON-NORTH | 2665013 | 13 | Silverton | Marion | Y | BR2 | 28 | 11.7 | 17.8 | 2.6746 | 0 | 3.1215 | 3.1215
SILVERTON | SILVERTON-WEST | 2665033 | 13 | Silverton | Marion | Y | BR2 | 28 | 9.4 | 17.8 | 1.4311 | 7.37 | 2.3475 | -5.0225
SIX CORNERS | SIX CORNERS-13359 | 4670013 | 13 | Six Corners | Washington | Y | WR1 | 21 | 11.8 | 17.8 | 0.39592 | 0 | 3.7782 | 3.7782
SIX CORNERS | SIX CORNERS-13360 | 4670023 | 13 | Six Corners | Washington | Y | WR1 | 21 | 6 | 17.8 | 0.14482 | 0 | 1.6461 | 1.6461
SIX CORNERS | SIX CORNERS-BORCHERS | 4670043 | 13 | Six Corners | Washington | Y | WR2 | 28 | 7.4 | 17.8 | 0.57506 | 0 | 2.0668 | 2.0668
SIX CORNERS | SIX CORNERS-CHAPMAN | 4670033 | 13 | Six Corners | Washington | Y | WR2 | 28 | 12.1 | 17.8 | 0.2797 | 0 | 3.2691 | 3.2691
SIX CORNERS | SIX CORNERS-SIX CORNERS 13 | 4670053 | 13 | Six Corners | Washington | Y | WR2 | 28 | 8.9 | 17.8 | 0.55163 | 0 | 3.3987 | 3.3987
SPRINGBROOK | SPRINGBROOK-ST PAUL | 4672023 | 13 | Newberg | Yamhill | Y | WR1 | 28 | 5.6 | 17.8 | 3.1158 | 0 | 0.27644 | 0.27644
SPRINGBROOK | SPRINGBROOK-VILLA | 4672013 | 13 | Newberg | Yamhill | Y | WR1 | 28 | 7.8366 | 17.8 | 0.61774 | 0 | 3.3633 | 3.3633
SPRINGBROOK | SPRINGBROOK-FERNWOOD | 4672043 | 13 | Newberg | Yamhill | Y | WR2 | 28 | 10.3 | 17.8 | 2.1089 | 0 | 2.4529 | 2.4529
SPRINGBROOK | SPRINGBROOK-ZIMRI | 4672063 | 13 | Newberg | Yamhill | Y | WR2 | 28 | 6.5265 | 17.8 | 0.36688 | 0 | 2.3434 | 2.3434
ST LOUIS | ST LOUIS-WEST | 2630023 | 13 | St. Louis | Marion | Y | BR1 | 7.5 | 6 | 17.8 | 0.09792 | 2.2 | 1.3523 | -0.84768
ST LOUIS | ST LOUIS-EAST | 2630013 | 13 | St. Louis | Marion | Y | BR4 | 16 | 9.2 | 17.8 | 0.18172 | 2 | 3.9323 | 1.9323
ST LOUIS | ST LOUIS-NORTH | 2630033 | 13 | St. Louis | Marion | Y | BR4 | 16 | 6.4 | 12.2 | 2.8216 | 0 | -0.78393 | -0.78393
ST MARYS EAST | ST MARYS EAST-BUTNER | 4635053 | 13 | near Beaverton | Washington | Y | WR7 | 28 | 0.1 | 17.8 | 0.199 | 0 | 0 | 0
ST MARYS EAST | ST MARYS EAST-MILLIKAN | 4635063 | 13 | near Beaverton | Washington | Y | WR7 | 28 | 6.7 | 14.3 | 0 | 0 | 2.7464 | 2.7464
ST MARYS EAST | ST MARYS EAST-ST MARYS 13 | 4635043 | 13 | near Beaverton | Washington | Y | WR7 | 28 | 0.9 | 17.8 | 0.02 | 0 | 0.27325 | 0.27325
ST MARYS EAST | ST MARYS EAST-BETHANY | 4635023 | 13 | near Beaverton | Washington | Y | WR8 | 28 | 6.6 | 17.8 | 0.0692 | 0 | 2.6096 | 2.6096
ST MARYS EAST | ST MARYS EAST-ELMONICA | 4635033 | 13 | near Beaverton | Washington | Y | WR8 | 28 | 9.8 | 17.8 | 0.11363 | 0 | 3.2359 | 3.2359
ST MARYS EAST | ST MARYS EAST-JENKINS | 4635013 | 13 | near Beaverton | Washington | Y | WR8 | 28 | 9.9 | 17.8 | 0.043 | 0 | 0.090176 | 0.090176
STEPHENS | STEPHENS-11001 11.1KV | 1385032 | 11 | Portland | Multnomah | Y | BK7 BK8 | 50 | 5.55 | 8.9 | 0.09475 | 0 | 1.6078 | 1.6078
STEPHENS | STEPHENS-11020 11.1KV | 1385042 | 11 | Portland | Multnomah | Y | BK7 BK8 | 50 | 2.34 | 8.9 | 0.031755 | 0 | 0.22854 | 0.22854
STEPHENS | STEPHENS-11098 11.1KV | 1385022 | 11 | Portland | Multnomah | Y | BK7 BK8 | 50 | 2.4 | 12.8 | 0 | 0 | 0.2122 | 0.2122
SULLIVAN | SULLIVAN-ROBINWOOD | 6675013 | 13 | West Linn | Clackamas | Y | WR8 | 16.8 | 8.14 | 17.8 | 0.13401 | 0 | 3.4318 | 3.4318
SULLIVAN | SULLIVAN-SUSSEX | 6675033 | 13 | West Linn | Clackamas | Y | WR8 | 16.8 | 3.8 | 18.4 | 0.18336 | 0 | 0.82109 | 0.82109
SULLIVAN | SULLIVAN-SALAMO | 6675053 | 13 | West Linn | Clackamas | Y | WR9 | 28 | 8.9 | 18.6 | 0.05577 | 0 | 2.0026 | 2.0026
SULLIVAN | SULLIVAN-TANNER | 6675023 | 13 | West Linn | Clackamas | Y | WR9 | 28 | 10.2 | 14.3 | 0.16817 | 0 | 2.8083 | 2.8083
SULLIVAN | SULLIVAN-WILLAMETTE | 6675043 | 13 | West Linn | Clackamas | Y | WR9 | 28 | 6.51 | 17.8 | 0.15084 | 0 | 0.86618 | 0.86618
SUMMIT | SUMMIT-GOVERNMENT CAMP | 5677023 | 13 | Government Camp | Clackamas | Y | FR2 | 14 | 2.2 | 10.7 | 0 | 0 | 0.40001 | 0.40001
SUMMIT | SUMMIT-MEADOWS | 5677013 | 13 | Government Camp | Clackamas | Y | FR2 | 14 | 3.7 | 5 | 0 | 0 | 0.23296 | 0.23296
SUMMIT | SUMMIT-SUMMIT 13 | 5677033 | 13 | Government Camp | Clackamas | Y | FR2 | 14 | 2.8 | 10.7 | 0 | 0 | 0.60464 | 0.60464
SUNSET | SUNSET-CORNELL | 4679133 | 13 | near Hillsboro | Washington | Y | WR1 | 50 | 5.33 | 15 | 0 | 0 | 4.9327 | 4.9327
SUNSET | SUNSET-YOUNG | 4679113 | 13 | near Hillsboro | Washington | Y | WR1 | 50 | 7.44 | 15 | 0.39468 | 0 | 3.1726 | 3.1726
SUNSET | SUNSET-PAULING | 4679213 | 13 | near Hillsboro | Washington | Y | WR2 | 50 | 4.32 | 15 | 4.5 | 0 | -0.71457 | -0.71457
SUNSET | SUNSET-SPALDING | 4679323 | 13 | near Hillsboro | Washington | Y | WR3 | 50 | 4.68 | 17 | 11.4 | 0 | 1.5776 | 1.5776
SUNSET | SUNSET-COLFAX | 4679453 | 13 | near Hillsboro | Washington | Y | WR4 | 50 | 5.7 | 17 | 0.1 | 0 | 4.1352 | 4.1352
SUNSET | SUNSET-MCCALL | 4679433 | 13 | near Hillsboro | Washington | Y | WR4 | 50 | 10 | 17 | 8.812 | 0 | -7.1268 | -7.1268
SUNSET | SUNSET-MEEK | 4679423 | 13 | near Hillsboro | Washington | Y | WR4 | 50 | 8.22 | 18.4 | 4.101 | 0 | 1.4667 | 1.4667
SUNSET | *REDACTED* | 4679244 | 34.5 | near Hillsboro | Washington | Y | WJ10 | 125 | *REDACTED* | 50 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679354 | 34.5 | near Hillsboro | Washington | Y | WJ11 | 125 | *REDACTED* | 50 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679364 | 34.5 | near Hillsboro | Washington | Y | WJ11 | 125 | *REDACTED* | 50 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679123 | 13 | near Hillsboro | Washington | Y | WR1 | 50 | *REDACTED* | 15 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679153 | 13 | near Hillsboro | Washington | Y | WR1 | 50 | *REDACTED* | 15 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679143 | 13 | near Hillsboro | Washington | Y | WR1 | 50 | *REDACTED* | 15 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679253 | 13 | near Hillsboro | Washington | Y | WR2 | 50 | *REDACTED* | 15 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679243 | 13 | near Hillsboro | Washington | Y | WR2 | 50 | *REDACTED* | 15 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679223 | 13 | near Hillsboro | Washington | Y | WR2 | 50 | *REDACTED* | 15 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679233 | 13 | near Hillsboro | Washington | Y | WR2 | 50 | *REDACTED* | 15 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679313 | 13 | near Hillsboro | Washington | Y | WR3 | 50 | *REDACTED* | 17 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679353 | 13 | near Hillsboro | Washington | Y | WR3 | 50 | *REDACTED* | 17 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679463 | 13 | near Hillsboro | Washington | Y | WR4 | 50 | *REDACTED* | 15 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679443 | 13 | near Hillsboro | Washington | Y | WR4 | 50 | *REDACTED* | 17 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679553 | 13 | near Hillsboro | Washington | Y | WR5 | 50 | *REDACTED* | 15 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679513 | 13 | near Hillsboro | Washington | Y | WR5 | 50 | *REDACTED* | 15 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679523 | 13 | near Hillsboro | Washington | Y | WR5 | 50 | *REDACTED* | 17 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679533 | 13 | near Hillsboro | Washington | Y | WR5 | 50 | *REDACTED* | 23.5 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679653 | 13 | near Hillsboro | Washington | Y | WR6 | 50 | *REDACTED* | 15 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679613 | 13 | near Hillsboro | Washington | Y | WR6 | 50 | *REDACTED* | 15 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679623 | 13 | near Hillsboro | Washington | Y | WR6 | 50 | *REDACTED* | 17 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679633 | 13 | near Hillsboro | Washington | Y | WR6 | 50 | *REDACTED* | 23.5 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679753 | 13 | near Hillsboro | Washington | Y | WR7 | 50 | *REDACTED* | 15 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679713 | 13 | near Hillsboro | Washington | Y | WR7 | 50 | *REDACTED* | 15 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679723 | 13 | near Hillsboro | Washington | Y | WR7 | 50 | *REDACTED* | 17 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679733 | 13 | near Hillsboro | Washington | Y | WR7 | 50 | *REDACTED* | 23.5 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679853 | 13 | near Hillsboro | Washington | Y | WR8 | 50 | *REDACTED* | 15 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679813 | 13 | near Hillsboro | Washington | Y | WR8 | 50 | *REDACTED* | 15 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679823 | 13 | near Hillsboro | Washington | Y | WR8 | 50 | *REDACTED* | 17 | 0 | 0 | *REDACTED* | 0
SUNSET | *REDACTED* | 4679833 | 13 | near Hillsboro | Washington | Y | WR8 | 50 | *REDACTED* | 23.5 | 0 | 0 | *REDACTED* | 0
SWAN ISLAND | *REDACTED* | 1680153 | 13 | Portland | Multnomah | Y | WR2 | 28 | *REDACTED* | 17.1 | 0 | 0 | *REDACTED* | 0
SWAN ISLAND | *REDACTED* | 1680143 | 13 | Portland | Multnomah | Y | WR2 | 28 | *REDACTED* | 18.4 | 0 | 0 | *REDACTED* | 0
TABOR | *REDACTED* | 1690033 | 13 | Portland | Multnomah | Y | WR6 | 22.4 | *REDACTED* | 16.8 | 0 | 0 | *REDACTED* | 0
SWAN ISLAND | SWAN ISLAND-BASIN | 1680073 | 13 | Portland | Multnomah | Y | WR1 | 22.4 | 7.99 | 18.4 | 0.1235 | 0 | 2.1991 | 2.1991
SWAN ISLAND | SWAN ISLAND-GOING | 1680133 | 13 | Portland | Multnomah | Y | WR1 | 22.4 | 6.9 | 17.8 | 0 | 0 | 1.2026 | 1.2026
SWAN ISLAND | SWAN ISLAND-DOLPHIN | 1680123 | 13 | Portland | Multnomah | Y | WR2 | 28 | 7.9 | 18.4 | 0.20124 | 0 | 1.3988 | 1.3988
*REDACTED* | *REDACTED* | 4693033 | 13 | Beaverton | Washington | Y | WR1 | 28 | *REDACTED* | 18.4 | 0 | 0 | *REDACTED* | 0
*REDACTED* | *REDACTED* | 4693023 | 13 | Beaverton | Washington | Y | WR1 | 28 | *REDACTED* | 17.8 | 0 | 0 | *REDACTED* | 0
SYLVAN | SYLVAN-BARNES | 1685013 | 13 | near Portland | Multnomah | N | WR1 | 22.4 | 9.1 | 17.8 | 2.1845 | 0 | 2.71 | 2.71
SYLVAN | SYLVAN-PATTON | 1685023 | 13 | near Portland | Multnomah | N | WR1 | 22.4 | 10 | 17.8 | 0.34416 | 0 | 4.2586 | 4.2586
TABOR | TABOR-82ND | 1690013 | 13 | Portland | Multnomah | Y | WR6 | 22.4 | 6.5 | 17.8 | 0.49238 | 0 | -0.010599 | -0.010599
TABOR | TABOR-TABOR 13 | 1690023 | 13 | Portland | Multnomah | Y | WR6 | 22.4 | 7.8 | 16.8 | 0.49147 | 0 | 2.5704 | 2.5704
*REDACTED* | *REDACTED* | 4693013 | 13 | Beaverton | Washington | Y | WR1 | 28 | *REDACTED* | 14.3 | 0 | 0 | *REDACTED* | 0
*REDACTED* | *REDACTED* | 4693063 | 13 | Beaverton | Washington | Y | WR2 | 28 | *REDACTED* | 14.3 | 0 | 0 | *REDACTED* | 0
*REDACTED* | *REDACTED* | 4693053 | 13 | Beaverton | Washington | Y | WR2 | 28 | *REDACTED* | 14.3 | 0 | 0 | *REDACTED* | 0
*REDACTED* | *REDACTED* | 4693043 | 13 | Beaverton | Washington | Y | WR2 | 28 | *REDACTED* | 17.8 | 0 | 0 | *REDACTED* | 0
*REDACTED* | *REDACTED* | 4693093 | 13 | Beaverton | Washington | Y | WR3 | 28 | *REDACTED* | 18.4 | 0 | 0 | *REDACTED* | 0
*REDACTED* | *REDACTED* | 4693083 | 13 | Beaverton | Washington | Y | WR3 | 28 | *REDACTED* | 18.4 | 0 | 0 | *REDACTED* | 0
*REDACTED* | *REDACTED* | 4693073 | 13 | Beaverton | Washington | Y | WR3 | 28 | *REDACTED* | 18.4 | 0 | 0 | *REDACTED* | 0
TOWN CENTER | *REDACTED* | 6696033 | 13 | Portland | Clackamas | Y | WR1 | 28 | *REDACTED* | 17.8 | 0 | 0 | *REDACTED* | 0
TOWN CENTER | *REDACTED* | 6696043 | 13 | Portland | Clackamas | Y | WR2 | 28 | *REDACTED* | 14.3 | 0 | 0 | *REDACTED* | 0
TUALATIN | *REDACTED* | 4697053 | 13 | Tualatin | Washington | Y | WR1 | 28 | *REDACTED* | 18.4 | 0 | 0 | *REDACTED* | 0
TIGARD | TIGARD-13336 | 4695013 | 13 | Tigard | Washington | Y | WR1 | 16.8 | 5 | 17.8 | 0.01816 | 0 | 1.7941 | 1.7941
TIGARD | TIGARD-13337 | 4695043 | 13 | Tigard | Washington | Y | WR1 | 16.8 | 4.9 | 17.8 | 0.080335 | 0 | 1.8086 | 1.8086
TIGARD | TIGARD-13361 | 4695023 | 13 | Tigard | Washington | Y | WR2 | 28 | 3.8 | 17.8 | 0.02283 | 0 | 1.1384 | 1.1384
TIGARD | TIGARD-13362 | 4695033 | 13 | Tigard | Washington | Y | WR2 | 28 | 9.3 | 17.8 | 0.25185 | 0 | 2.3529 | 2.3529
TIGARD | TIGARD-TIGARD 13 | 4695053 | 13 | Tigard | Washington | Y | WR2 | 28 | 7.2 | 17.8 | 0.16399 | 0 | 3.3651 | 3.3651
TOWN CENTER | TOWN CENTER-MONTEREY | 6696053 | 13 | Portland | Clackamas | Y | WR1 | 28 | 9.8 | 17.8 | 0.1201 | 0 | 4.2084 | 4.2084
TOWN CENTER | TOWN CENTER-SOUTH | 6696013 | 13 | Portland | Clackamas | Y | WR1 | 28 | 4.12 | 11 | 0 | 0 | 0.98529 | 0.98529
TOWN CENTER | TOWN CENTER-LAWNFIELD | 6696023 | 13 | Portland | Clackamas | Y | WR2 | 28 | 6.1 | 17.8 | 1.3189 | 0 | 2.5626 | 2.5626
TOWN CENTER | TOWN CENTER-NORTH | 6696073 | 13 | Portland | Clackamas | Y | WR2 | 28 | 3.6 | 11 | 0 | 0 | 0.54087 | 0.54087
TOWN CENTER | TOWN CENTER-SUNNYBROOK | 6696063 | 13 | Portland | Clackamas | Y | WR2 | 28 | 7.4 | 17.8 | 0.13084 | 0 | 2.6474 | 2.6474
URBAN | *REDACTED* | 1707083 | 13 | Portland | Multnomah | Y | WR1 | 28 | *REDACTED* | 17.8 | 0 | 0 | *REDACTED* | 0
URBAN | *REDACTED* | 1707093 | 13 | Portland | Multnomah | Y | WR2 | 22.4 | *REDACTED* | 17.8 | 0 | 0 | *REDACTED* | 0
TUALATIN | TUALATIN-HERMAN | 4697043 | 13 | Tualatin | Washington | Y | WR1 | 28 | 6.1 | 17.8 | 0.14427 | 0 | 1.2342 | 1.2342
TUALATIN | TUALATIN-TUALATIN 13 | 4697033 | 13 | Tualatin | Washington | Y | WR1 | 28 | 7.9 | 17.8 | 0.077 | 0 | 1.7425 | 1.7425
TUALATIN | TUALATIN-AVERY | 4697023 | 13 | Tualatin | Washington | Y | WR2 | 28 | 9.2 | 17.8 | 1.0826 | 0 | 2.5195 | 2.5195
TUALATIN | TUALATIN-CIPOLE | 4697063 | 13 | Tualatin | Washington | Y | WR2 | 28 | 12.3 | 17.8 | 1.5892 | 0 | 2.5493 | 2.5493
TUALATIN | TUALATIN-IBACH | 4697013 | 13 | Tualatin | Washington | Y | WR2 | 28 | 9.3 | 17.8 | 0.28156 | 0 | 2.5454 | 2.5454
URBAN | *REDACTED* | 1707033 | 13 | Portland | Multnomah | Y | WR3 | 28 | *REDACTED* | 14.3 | 0 | 0 | *REDACTED* | 0
TURNER | TURNER-CASCADE | 2698023 | 13 | Turner | Marion | N | WR1 | 8.4 | 3.915 | 14.3 | 4.6043 | 0 | 0.06 | 0.06
TURNER | TURNER-TURNER 13 | 2698013 | 13 | Turner | Marion | N | WR1 | 8.4 | 4.7 | 14.3 | 0.50769 | 2.1599 | 1.505 | -0.65493
TWILIGHT | TWILIGHT-BREMER | 6699033 | 13 | Canby | Clackamas | Y | BR1 | 28 | 6.78 | 7.3 | 0.25316 | 0 | 2.1047 | 2.1047
UNIONVALE | UNIONVALE-UNIONVALE 13 | 4700013 | 13 | Dayton | Yamhill | N | BR1 | 7.5 | 5.7 | 10.7 | 0.18096 | 0 | 1.795 | 1.795
UNIVERSITY | UNIVERSITY-MILL | 2705013 | 13 | Salem | Marion | N | WR3 | 22.4 | 7 | 17.8 | 0.0099 | 0 | 3.7047 | 3.7047
UNIVERSITY | UNIVERSITY-TRADE | 2705023 | 13 | Salem | Marion | N | WR3 | 22.4 | 6.32 | 17.8 | 0.056075 | 0 | 2.4957 | 2.4957
URBAN | URBAN-CORBETT | 1707013 | 13 | Portland | Multnomah | Y | WR1 | 28 | 3.3 | 10.4 | 0.05127 | 0 | 1.2092 | 1.2092
URBAN | URBAN-GIBBS | 1707043 | 13 | Portland | Multnomah | Y | WR1 | 28 | 5.81 | 10.4 | 5.6483 | 0 | 2.5766 | 2.5766
URBAN | URBAN-BARBUR | 1707053 | 13 | Portland | Multnomah | Y | WR2 | 22.4 | 6.97 | 17.8 | 0.0919 | 0 | 3.005 | 3.005
URBAN | URBAN-KELLY | 1707073 | 13 | Portland | Multnomah | Y | WR2 | 22.4 | 6.35 | 17.8 | 4.0115 | 0 | -1.4224 | -1.4224
URBAN | URBAN-TEMP NORTH | 1707103 | 13 | Portland | Multnomah | Y | WR20 | 28 | 6.54 | 17.8 | 0 | 0 | 0 | 0
URBAN | URBAN-TEMP SOUTH | 1707113 | 13 | Portland | Multnomah | Y | WR20 | 28 | 0.4 | 17.8 | 0 | 0 | 0 | 0
URBAN | URBAN-GAINES | 1707063 | 13 | Portland | Multnomah | Y | WR3 | 28 | 6.68 | 10.4 | 0.01545 | 0 | 3.3881 | 3.3881
URBAN | URBAN-LANDING | 1707023 | 13 | Portland | Multnomah | Y | WR3 | 28 | 7.13 | 13.7 | 0.149 | 0 | 1.1027 | 1.1027
*REDACTED* | *REDACTED* | 1743013 | 13 | Portland | Multnomah | Y | WR1 | 28 | *REDACTED* | *REDACTED* | 0 | 0 | *REDACTED* | 0
*REDACTED* | *REDACTED* | 1743023 | 13 | Portland | Multnomah | Y | WR2 | 28 | *REDACTED* | *REDACTED* | 0 | 0 | *REDACTED* | 0
WACONDA | *REDACTED* | 2720033 | 13 | near Hopmere | Marion | Y | BR2 | 15.6 | *REDACTED* | 17.8 | 0 | 0 | *REDACTED* | 0
WILLAMINA | *REDACTED* | 2740013 | 13 | near Willamina | Polk | Y | BR2 | 7.5 | *REDACTED* | 17.8 | 0 | 0 | *REDACTED* | 0
PENINSULA PARK | PENINSULA PARK-PENINSULA PARK 13 | 1545011 | 13 | Portland | Multnomah | Y | WR1 | 28 | 6.23 | 17.8 | 0.06716 | 0 | 1.7028 | 1.7028
WACONDA | WACONDA-RIVER | 2720023 | 13 | near Hopmere | Marion | Y | BR1 | 25 | 6 | 17.8 | 0.28679 | 1.9801 | 0.44818 | -1.5319
WACONDA | WACONDA-WACONDA 13 | 2720013 | 13 | near Hopmere | Marion | Y | BR1 | 25 | 7.5 | 14.3 | 3.0494 | 4.75 | -1.1563 | -5.9063
RIVERGATE SOUTH | RIVERGATE SOUTH-SWIFT | 1598013 | 13 | near Portland | Multnomah | Y | WR3 | 22.4 | 3.88 | 17.8 | 0 | 0 | 0.80809 | 0.80809
WALLACE | WALLACE-WALLACE 13 | 2725013 | 13 | Salem | Polk | Y | BR1 | 28 | 4.9607 | 14.3 | 2.5067 | 2.5 | -0.65975 | -3.1597
WALLACE | WALLACE-WILLOW LAKE | 2725023 | 13 | Salem | Polk | Y | BR1 | 28 | 5.0144 | 14.3 | 0.04824 | 0 | 1.7082 | 1.7082
WELCHES | WELCHES-ZIG ZAG | 5727023 | 13 | near Welches | Clackamas | Y | BR1 | 7.5 | 4.5 | 7.3 | 0.0042 | 0 | 0.81449 | 0.81449
WELCHES | WELCHES-WELCHES 13 | 5727013 | 13 | near Welches | Clackamas | Y | BR3 | 10.5 | 7.8 | 10.4 | 0 | 0 | 2.0698 | 2.0698
WEST PORTLAND | WEST PORTLAND-PACIFIC | 4735043 | 13 | Lower Yard near Tigard | Washington | Y | WR1 | 28 | 9.6 | 17.8 | 0.14118 | 0 | 4.0116 | 4.0116
WEST PORTLAND | WEST PORTLAND-WEST PORTLAND 13 | 4735013 | 13 | Lower Yard near Tigard | Washington | Y | WR1 | 28 | 8.8 | 17.8 | 0.39475 | 0 | 2.3552 | 2.3552
WEST PORTLAND | WEST PORTLAND-72ND | 4735033 | 13 | Lower Yard near Tigard | Washington | Y | WR2 | 28 | 9.7 | 17.8 | 0.47868 | 0 | 3.8084 | 3.8084
WEST PORTLAND | WEST PORTLAND-NORTH | 4735023 | 13 | Lower Yard near Tigard | Washington | Y | WR2 | 28 | 6.8 | 17.8 | 0.16206 | 0 | 2.5369 | 2.5369
WEST UNION | WEST UNION-CORNELIUS PASS | 4737013 | 13 | near Hillsboro | Washington | Y | WR1 | 28 | 7.33 | 17.8 | 0.92902 | 0 | 0.7445 | 0.7445
WEST UNION | WEST UNION-WEST UNION 13 | 4737023 | 13 | near Hillsboro | Washington | Y | WR1 | 28 | 11.43 | 17.8 | 4.629 | 0 | 2.2278 | 2.2278
WEST UNION | WEST UNION-ALOCLEK | 4737033 | 13 | near Hillsboro | Washington | Y | WR2 | 28 | 6.92 | 18.4 | 8.5 | 0 | -2.2059 | -2.2059
SILVERTON | SILVERTON-GARDEN | 2665043 | 13 | Silverton | Marion | Y | BR1 | 14 | 0 | 17.8 | 0 | 0 | 0 | 0
WEST UNION | WEST UNION-IMBRIE | 4737053 | 13 | near Hillsboro | Washington | Y | WR2 | 28 | 4.8 | 18.4 | 0 | 0 | 4.1173 | 4.1173
WEST UNION | WEST UNION-HOPS | 4737063 | 13 | near Hillsboro | Washington | Y | WR2 | 28 | 0 | 18.4 | 0 | 0 | 0 | 0
WILLAMINA | WILLAMINA-BRIDGE | 2740033 | 13 | near Willamina | Polk | Y | BR1 | 16.8 | 4.1404 | 9.9 | 0.05136 | 2.97 | 1.4433 | -1.5267
WILLAMINA | WILLAMINA-BUELL | 2740023 | 13 | near Willamina | Polk | Y | BR1 | 16.8 | 4.6961 | 10.4 | 3.1229 | 4.7 | -1.0005 | -5.7005
WEST UNION | WEST UNION-JACOBSON | 4737043 | 13 | near Hillsboro | Washington | Y | WR2 | 28 | 9.19 | 18.4 | 0 | 0 | 2.6342 | 2.6342
WILLBRIDGE | WILLBRIDGE-WILLBRIDGE 1 11.4KV | 1741012 | 11 | Portland | Multnomah | N | WK1 | 20 | 2.3 | 9.5 | 0 | 0 | 0.75 | 0.75
WILLBRIDGE | WILLBRIDGE-WILLBRIDGE 4 11.4KV | 1741042 | 11 | Portland | Multnomah | N | WK1 | 20 | 4.9 | 12.2 | 0.026 | 0 | 1.57 | 1.57
WILSONVILLE | WILSONVILLE-BOECKMAN | 4745073 | 13 | near Wilsonville | Clackamas | Y | WR1 | 28 | 5 | 17.8 | 0.20045 | 0 | 1.3122 | 1.3122
WILSONVILLE | WILSONVILLE-CHARBONNEAU | 4745063 | 13 | near Wilsonville | Clackamas | Y | WR1 | 28 | 11.4 | 18.4 | 0.39944 | 2.16 | 4.6101 | 2.4501
WILSONVILLE | WILSONVILLE-MENTORTEK | 4745043 | 13 | near Wilsonville | Clackamas | Y | WR2 | 28 | 9 | 18.4 | 4 | 0 | 2.9672 | 2.9672
WILSONVILLE | WILSONVILLE-WEST | 4745093 | 13 | near Wilsonville | Clackamas | Y | WR2 | 28 | 8.9 | 18.4 | 0.28819 | 0 | 3.4075 | 3.4075
WILSONVILLE | WILSONVILLE-CITY | 4745013 | 13 | near Wilsonville | Clackamas | Y | WR3 | 28 | 11 | 18.4 | 0.031755 | 0 | 4.6593 | 4.6593
WILSONVILLE | WILSONVILLE-PARKWAY | 4745023 | 13 | near Wilsonville | Clackamas | Y | WR3 | 28 | 7.6 | 18.4 | 2 | 0 | 2.8713 | 2.8713
WOODBURN | WOODBURN-CANNERY | 2753033 | 13 | Woodburn | Marion | Y | BR1 | 28 | 9.3 | 17.8 | 0.17319 | 0 | 3.1162 | 3.1162
WOODBURN | WOODBURN-TOMLIN | 2753023 | 13 | Woodburn | Marion | Y | BR1 | 28 | 8.4 | 18.4 | 0.52093 | 2.9884 | 3.8277 | 0.83922
WOODBURN | WOODBURN-EAST | 2753013 | 13 | Woodburn | Marion | Y | BR2 | 14 | 2.2 | 10.4 | 0.43876 | 6.5 | 0.62681 | -5.8732
WOODBURN | WOODBURN-WEST | 2753043 | 13 | Woodburn | Marion | Y | BR2 | 14 | 7.6 | 17.8 | 2.3829 | 0 | 1.9947 | 1.9947
YAMHILL | YAMHILL-YAMHILL 13 | 4760013 | 13 | near Yamhill | Yamhill | N | BR1 | 7.5 | 8.19 | 17.8 | 0.75002 | 2.5 | 2.5068 | 0.0068042
YAMHILL | YAMHILL-CARLTON | 4760023 | 13 | near Yamhill | Yamhill | N | BR2 | 7.8 | 9.215 | 10.4 | 0.4527 | 0 | 2.7934 | 2.7934