## Summary Formatted
Disclaimer: 1. The data provided in the spreadsheet represents a high-level overview of certain limited pieces of information about Pacific Power’s Oregon distribution system and queue. 2. The data represents the best available information at the time of posting, which means it does not necessarily reflect current conditions in any given area. 3. This data is being provided on a non-binding, informational basis only, and should not be interpreted in any way as indicating or implying that a certain area may (or may not) be able to interconnect additional generation, or what the cost or timing requirements associated with interconnection in a certain area may be. 4. The data in this spreadsheet is not intended to replace any existing interconnection service request and study processes, any transmission service request and study processes, any state or federal distribution or transmission planning processes, any existing load projection or forecasting processes, or any other existing processes that may consider the data in this spreadsheet as a single component of a broader evaluation. 5. Pacific Power shall not be held liable under any circumstances for any errors, omissions, inaccurate, and/or out-of-date content or information provided. 6. MDL values highlighted in orange indicate that the values are an estimation based on historic loading data. Actual values may vary significantly from the values provided.
Data as of August 4, 2020
Substation Name | Feeder Voltage | No. of Transformers | No. of Feeders | Area | Load Pocket | County | Feeder SCADA Y/N (Refer to Definitions tab for details) | Customer Sensitive Y/N | Feeder Name/Designation | Feeder Load Peak (Summer) (Refer to Definitions tab for details) |  | Feeder Capacity (Summer) (Refer to Definitions tab for details) |  | Existing DER Connected (MW) (Refer to Definitions tab for details) | Proposed DER in Queue (MW) (Refer to Definitions tab for details) | Minimum Daytime Load (Refer to Definitions tab for details)
Agness | 115-12.5 kV | 1 | 3 | Medford | Grants Pass | Jackson | Y | N | 5R172 | 3.6 | MW | 10.3 | MVA | 0.07009 | 0 | 1 | MW
Agness | 115-12.5 kV | 1 | 3 | Medford | Grants Pass | Jackson | Y | N | 5R173 | 7.3 | MW | 10.3 | MVA | 0.12631 | 0 | 3.2 | MW
Agness | 115-12.5 kV | 1 | 3 | Medford | Grants Pass | Jackson | Y | N | 5R322 | 9.5 | MW | 10.3 | MVA | 0.11372 | 0 | 1.7 | MW
Albina | 115-11.7 kV | 2 | 8 | Portland | Portland | Multnomah | Y | Y | 5P111 | Redacted | MW | 8.9 | MVA | 0 | 0 | Redacted | MW
Albina | 115-11.7 kV | 2 | 8 | Portland | Portland | Multnomah | Y | Y | 5P194 | Redacted | MW | 8.9 | MVA | 0 | 0 | Redacted | MW
Albina | 115-11.7 kV | 2 | 8 | Portland | Portland | Multnomah | Y | Y | 5P196 | Redacted | MW | 8.9 | MVA | 0.0072 | 0 | Redacted | MW
Albina | 115-11.7 kV | 2 | 8 | Portland | Portland | Multnomah | Y | Y | 5P200 | Redacted | MW | 8.9 | MVA | 0.48314 | 0 | Redacted | MW
Albina | 115-11.7 kV | 2 | 8 | Portland | Portland | Multnomah | Y | Y | 5P91 | Redacted | MW | 8.9 | MVA | 0 | 0 | Redacted | MW
Albina | 115-11.7 kV | 2 | 8 | Portland | Portland | Multnomah | Y | Y | 5P92 | Redacted | MW | 8.9 | MVA | 0.018 | 0 | Redacted | MW
Alderwood | 69-12.5 kV | 2 | 4 | Portland | Portland | Multnomah | Y | N | 5P22 | 7.55 | MW | 10.3 | MVA | 0 | 0 | 2.6 | MW
Alderwood | 69-12.5 kV | 2 | 4 | Portland | Portland | Multnomah | Y | Y | 5P23 | Redacted | MW | 10.3 | MVA | 0 | 0 | Redacted | MW
Alderwood | 69-12.5 kV | 2 | 4 | Portland | Portland | Multnomah | Y | N | 5P33 | 7.4 | MW | 10.3 | MVA | 0 | 0 | 2.58 | MW
Alderwood | 69-12.5 kV | 2 | 4 | Portland | Portland | Multnomah | Y | N | 5P604 | 7.5 | MW | 10.3 | MVA | 0.49728 | 0 | 2.33 | MW
Applegate | 115-12.5 kV | 1 | 2 | Medford | Grants Pass | Jackson | Y | N | 5R267 | 4.6 | MW | 10.3 | MVA | 0.15859 | 0 | 1.7 | MW
Applegate | 115-12.5 kV | 1 | 2 | Medford | Grants Pass | Jackson | Y | N | 5R278 | 5.8 | MW | 10.3 | MVA | 0.13949 | 0 | 1.9 | MW
Enterprise | 69-20.8kV | 1 | 1 | Enterprise | Enterprise | Wallowa | N | N | 4W8 | 7 | MW | 9.8 | MVA | 1.5613 | 0 | -2.1 | MW
Ashland | 115-12.5 kV | 1 | 2 | Medford | Ashland | Jackson | Y | N | 5R241 | N/A | MW | N/A | MVA | 0 | 0 | N/A | MW
Ashland | 115-12.5 kV | 1 | 2 | Medford | Ashland | Jackson | Y | Y | 5R245 | Redacted | MW | 10.3 | MVA | 0.5942 | 0 | Redacted | MW
Enterprise | 69-12.5kV | 1 | 2 | Enterprise | Enterprise | Wallowa | N | N | 5W15 | 2.5 | MW | 9.8 | MVA | 0.44209 | 0 | 0.25791 | MW
Enterprise | 69-12.5kV | 1 | 2 | Enterprise | Enterprise | Wallowa | N | N | 5W26 | 2.8 | MW | 9.8 | MVA | 0.26842 | 0.36 | 0.98 | MW
Bandon Tie BPA | 12-20.8 kV | 1 | 1 | Bandon | Bandon | Coos | Y | N | L804 | 2 | MW | 6.55 | MVA | 0.01604 | 0 | 0.4977 | MW
Beacon | 69-12.5 kV | 1 | 2 | Medford | Grants Pass | Jackson | N | N | 5R104 | 4.2 | MW | 7.1 | MVA | 0.02998 | 0 | 1.1 | MW
Beacon | 69-12.5 kV | 1 | 2 | Medford | Grants Pass | Jackson | N | N | 5R105 | 3.2 | MW | 7.1 | MVA | 0.02322 | 0 | 0.6928 | MW
Beall Lane | 115-12.5 kV | 1 | 3 | Medford | Medford | Jackson | Y | N | 5R359 | 6.3 | MW | 10.3 | MVA | 0 | 0 | 0.4 | MW
Beall Lane | 115-12.5 kV | 1 | 3 | Medford | Medford | Jackson | Y | N | 5R361 | 7 | MW | 10.3 | MVA | 0.03117 | 0 | 2.2 | MW
Beall Lane | 115-12.5 kV | 1 | 3 | Medford | Medford | Jackson | Y | N | 5R364 | 7.7 | MW | 10.3 | MVA | 0.02894 | 0 | 1.9 | MW
Beatty | 69-12.5 kV | 1 | 1 | Beatty | Beatty | Klamath | N | N | 5L1 | 2.5 | MW | 5.1 | MVA | 0.03918 | 0.594 | 0.88 | MW
Belknap | 69-12.5 kV | 2 | 4 | Medford | Medford | Jackson | N | N | 5R1 | 6.8 | MW | 10.3 | MVA | 0.35485 | 0 | 1.2966 | MW
Belknap | 69-12.5 kV | 2 | 4 | Medford | Medford | Jackson | N | N | 5R2 | 8.4 | MW | 10.3 | MVA | 0.02828 | 0 | 2.1 | MW
Belknap | 69-12.5 kV | 2 | 4 | Medford | Medford | Jackson | N | N | 5R3 | 8.6 | MW | 10.3 | MVA | 0.21882 | 0 | 1.7959 | MW
Belknap | 69-12.5 kV | 2 | 4 | Medford | Medford | Jackson | N | N | 5R47 | 8.7 | MW | 10.3 | MVA | 0.08597 | 0 | 2.3 | MW
Bend Plant | 69-12.5kV | 3 | 4 | Bend | Bend | Deschutes | Y | N | 5D10 | 5.7 | MW | 8.6 | MVA | 0.37684 | 0 | 2 | MW
Bend Plant | 69-12.5kV | 3 | 4 | Bend | Bend | Deschutes | N | N | 5D11 | 4.2 | MW | 8.6 | MVA | 0.09762 | 0 | 0.95 | MW
Bend Plant | 69-12.5kV | 3 | 4 | Bend | Bend | Deschutes | Y | N | 5D12 | 3.2 | MW | 8.6 | MVA | 0.04255 | 0 | 1.3 | MW
Bend Plant | 69-12.5kV | 3 | 4 | Bend | Bend | Deschutes | Y | N | 5D196 | 4.3 | MW | 10.3 | MVA | 0.14677 | 0 | 1.7 | MW
Joseph | 20.8-12.47 kV | 1 | 1 | Enterprise | Enterprise | Wallowa | N | N | 5W21 | 2.1 | MW | 2.9 | MVA | 0.59758 | 0 | 0.06742 | MW
Bloss | 115-12.5 kV | 2 | 2 | Portland | Portland | Multnomah | Y | Y | 5P170 | Redacted | MW | 9.5 | MVA | 0 | 0 | Redacted | MW
Bloss | 115-12.5 kV | 2 | 2 | Portland | Portland | Multnomah | Y | Y | 5P172 | Redacted | MW | 10.3 | MVA | 0 | 0 | Redacted | MW
Bly | 69-12.5 kV | 1 | 1 | Bly | Bly | Klamath | N | N | 5L14 | 1.4 | MW | 6.9 | MVA | 10.752 | 3 | -12.983 | MW
Boise Cascade | 69-4 kV | 1 | 1 | Chiloquin | Chiloquin | Klamath | N | Y | 7L9 | Redacted | MW | 9.166 | MVA | 0 | 0 | Redacted | MW
Bonanza | 69-12.5 kV | 1 | 1 | Bonanza | Bonanza | Klamath | N | N | 5L7 | 4.911 | MW | 8.6 | MVA | 0.4963 | 0 | 0 | MW
Bond Street | 69-12.5kV | 1 | 3 | Bend | Bend | Deschutes | Y | N | 5D411 | 7.6 | MW | 10.3 | MVA | 0.38719 | 0 | 3.3 | MW
Bond Street | 69-12.5kV | 1 | 3 | Bend | Bend | Deschutes | Y | N | 5D413 | 6.2 | MW | 10.3 | MVA | 0.05885 | 0 | 1.7 | MW
Bond Street | 69-12.5kV | 1 | 3 | Bend | Bend | Deschutes | Y | N | 5D418 | 2.2 | MW | 10.3 | MVA | 0.11825 | 0 | 0.65 | MW
Brookhurst | 115-12.5 kV | 2 | 5 | Medford | Medford | Jackson | Y | N | 5R118 | 8.5 | MW | 10.3 | MVA | 0.32031 | 0 | 2.3 | MW
Brookhurst | 115-12.5 kV | 2 | 5 | Medford | Medford | Jackson | Y | N | 5R135 | 6.8 | MW | 10.3 | MVA | 0.06489 | 0 | 1.5 | MW
Brookhurst | 115-12.5 kV | 2 | 5 | Medford | Medford | Jackson | Y | N | 5R32 | 8.1 | MW | 10.3 | MVA | 0.14118 | 0 | 2 | MW
Brookhurst | 115-12.5 kV | 2 | 5 | Medford | Medford | Jackson | Y | N | 5R33 | 6.6 | MW | 10.3 | MVA | 0.08912 | 0 | 2 | MW
Brookhurst | 115-12.5 kV | 2 | 5 | Medford | Medford | Jackson | Y | N | 5R75 | 6.7 | MW | 10.3 | MVA | 0.07818 | 0 | 2.3 | MW
Brownsville | 69-20.8kV | 1 | 1 | Junction City | Albany/Corvallis/Stayton | Linn | N | N | 4M17 | 8.2 | MW | 13.125 | MVA | 0.09796 | 2.16 | 2.87 | MW
Bryant | 69-12.5 kV | 2 | 4 | Klamath Falls | Klamath Falls | Klamath | N | N | 5L2 | 6 | MW | 9 | MVA | 0.05517 | 0 | 1.4848 | MW
Bryant | 69-12.5 kV | 2 | 4 | Klamath Falls | Klamath Falls | Klamath | N | N | 5L3 | 5.4 | MW | 9 | MVA | 0.06149 | 0 | 1.5485 | MW
Bryant | 69-12.5 kV | 2 | 4 | Klamath Falls | Klamath Falls | Klamath | N | N | 5L4 | 5.22 | MW | 9 | MVA | 0.125 | 0 | 1.3485 | MW
Bryant | 69-12.5 kV | 2 | 4 | Klamath Falls | Klamath Falls | Klamath | N | N | 5L5 | 5.8 | MW | 9 | MVA | 0.12328 | 0 | 1.8717 | MW
Buchanan | 115-21.8kV | 2 | 3 | Willamette | Albany/Corvallis/Stayton | Benton | N | Y | 4M130 | Redacted | MW | 11.9 | MVA | 0.46507 | 0 | Redacted | MW
Buchanan | 115-21.8kV | 2 | 3 | Willamette | Albany/Corvallis/Stayton | Benton | N | N | 4M133 | 10.25 | MW | 15.9 | MVA | 4.3755 | 0 | -1.2755 | MW
Buchanan | 115-21.8kV | 2 | 3 | Willamette | Albany/Corvallis/Stayton | Benton | N | N | 4M134 | 7.41 | MW | 15.9 | MVA | 0.24444 | 0 | 1.9556 | MW
Minam | 69-12.47 kV | 1 | 1 | Enterprise | Enterprise | Wallowa | N | N | 5W18 | 0.047 | MW | 2.9 | MVA | 0 | 0 | 0.009 | MW
Pallette | 40-20kV | 1 | 2 | Enterprise | Enterprise | Wallowa | N | N | 4W14 | 0.3 | MW | 0.6 | MVA | 0.01044 | 0 | 0.1 | MW
Pallette | 40-20kV | 1 | 2 | Enterprise | Enterprise | Wallowa | N | N | 4W15 | 0.1 | MW | 0.6 | MVA | 0 | 0 | 0 | MW
Calapooya | 69-20.8kV | 1 | 2 | Lebanon | Albany/Corvallis/Stayton | Linn | Y | Y | 4M851 | Redacted | MW | 11.9 | MVA | 0 | 0 | Redacted | MW
Calapooya | 69-20.8kV | 1 | 2 | Lebanon | Albany/Corvallis/Stayton | Linn | Y | N | 4M850 | 2.95 | MW | 11.9 | MVA | 0.03687 | 0 | 1.09 | MW
Circle Blvd | 115-21.8kV | 2 | 3 | Willamette | Albany/Corvallis/Stayton | Benton | Y | Y | 4M396 | Redacted | MW | 20.5 | MVA | 0 | 0 | Redacted | MW
Circle Blvd | 115-21.8kV | 2 | 3 | Willamette | Albany/Corvallis/Stayton | Benton | Y | Y | 4M428 | Redacted | MW | 20.5 | MVA | 0 | 0 | Redacted | MW
Circle Blvd | 115-21.8kV | 2 | 3 | Willamette | Albany/Corvallis/Stayton | Benton | Y | Y | 4M430 | Redacted | MW | 20.5 | MVA | 0 | 0 | Redacted | MW
Campbell | 115-12.5 kV | 2 | 4 | Medford | Medford | Jackson | Y | N | 5R216 | 5.8 | MW | 10.3 | MVA | 0.007 | 0 | 2.2 | MW
Campbell | 115-12.5 kV | 2 | 4 | Medford | Medford | Jackson | Y | N | 5R218 | 5.2 | MW | 10.3 | MVA | 0.08362 | 0 | 2.2 | MW
Campbell | 115-12.5 kV | 2 | 4 | Medford | Medford | Jackson | Y | N | 5R227 | 6.1 | MW | 10.3 | MVA | 0.21774 | 0 | 2.013 | MW
Campbell | 115-12.5 kV | 2 | 4 | Medford | Medford | Jackson | Y | N | 5R312 | 7.4 | MW | 10.3 | MVA | 0.055 | 1.75 | 0.65 | MW
Cannon Beach | 115-12.5 kV | 1 | 2 | Cannon Beach | Cannon Beach | Clatsop | Y | N | 5A10 | 2.6 | MW | 10.3 | MVA | 0.05688 | 0 | 1.02 | MW
Cannon Beach | 115-12.5 kV | 1 | 2 | Cannon Beach | Cannon Beach | Clatsop | Y | N | 5A8 | 2.4 | MW | 10.3 | MVA | 0.00982 | 0 | 0.706 | MW
Coos River | 115-20.8 kV | 1 | 1 | Coos Bay | Coos Bay | Coos | N | N | 4C106 | 2.25 | MW | 7.56 | MVA | 0.03933 | 0 | 0.7875 | MW
Coquille | 115-20.8 kV | 2 | 3 | Coquille | Coquille | Coos | Y | N | 4C41 | 3.9 | MW | 15.948 | MVA | 0.00672 | 0 | 1.9897 | MW
Coquille | 115-20.8 kV | 2 | 3 | Coquille | Coquille | Coos | Y | N | 4C42 | 3 | MW | 7.7 | MVA | 0.01549 | 0 | 1.5125 | MW
Casebeer | 69-20.8 kV | 1 | 1 | Klamath Falls | Klamath Falls | Klamath | Y | N | 4L16 | 7.1 | MW | 13.9 | MVA | 5.2914 | 3 | -6.567 | MW
Cave Junction | 69-12.5 kV | 1 | 2 | Medford | Cave Junction | Jackson | Y | N | 5R52 | 6.9 | MW | 9.2 | MVA | 0.22508 | 3 | 3.6 | MW
Cave Junction | 69-12.5 kV | 1 | 2 | Medford | Cave Junction | Jackson | Y | N | 5R53 | 4.9 | MW | 9.2 | MVA | 0.05066 | 0 | 2.5 | MW
Caveman | 115-12.5 kV | 2 | 4 | Medford | Grants Pass | Jackson | Y | N | 5R295 | 5 | MW | 10.3 | MVA | 0.01253 | 0 | 1.3 | MW
Caveman | 115-12.5 kV | 2 | 4 | Medford | Grants Pass | Jackson | Y | N | 5R82 | 4.7 | MW | 9.5 | MVA | 0.06633 | 0 | 1.3 | MW
Caveman | 115-12.5 kV | 2 | 4 | Medford | Grants Pass | Jackson | Y | N | 5R98 | 4.6 | MW | 10.3 | MVA | 0 | 0 | 1.4 | MW
Caveman | 115-12.5 kV | 2 | 4 | Medford | Grants Pass | Jackson | Y | N | 5R99 | 5.1 | MW | 9.5 | MVA | 0.07182 | 0 | 1.5 | MW
Cherry Lane | 69-12.5kV | 1 | 1 | Madras | Madras | Jefferson | Y | N | 5D295 | 6.8 | MW | 10.3 | MVA | 10 | 0 | -8.3 | MVA
Chiloquin | 230-12.5 kV | 1 | 1 | Chiloquin | Chiloquin | Klamath | Y | N | 5L57 | 2.22 | MW | 11.5 | MVA | 10.1019 | 0 | -8.07 | MW
Chiloquin Market | 115-12.5 kV | 1 | 1 | Chiloquin | Chiloquin | Klamath | N | N | 5L37 | 1.4 | MW | 5.2 | MVA | 0.04613 | 0 | 0.36617 | MW
China Hat | 69-12.5kV | 1 | 3 | Bend | Bend | Deschutes | N | N | 5D140 | 5.6 | MW | 10.3 | MVA | 0.05777 | 0 | 1.8 | MW
China Hat | 69-12.5kV | 1 | 3 | Bend | Bend | Deschutes | N | N | 5D142 | 5.6 | MW | 10.3 | MVA | 0.04901 | 0 | 1.7 | MW
China Hat | 69-12.5kV | 1 | 3 | Bend | Bend | Deschutes | N | N | 5D144 | 5.6 | MW | 10.3 | MVA | 0.15715 | 0 | 1.8771 | MW
Circle Blvd | 115-21.8kV | 2 | 3 | Willamette | Albany/Corvallis/Stayton | Benton | Y | Y | 4M394 | Redacted | MW | 20.5 | MVA | 0 | 0 | Redacted | MW
Circle Blvd | 115-21.8kV | 2 | 3 | Willamette | Albany/Corvallis/Stayton | Benton | Y | Y | 4M427 | Redacted | MW | 20.5 | MVA | 0 | 0 | Redacted | MW
Circle Blvd | 115-21.8kV | 2 | 3 | Willamette | Albany/Corvallis/Stayton | Benton | Y | Y | 4M429 | Redacted | MW | 20.5 | MVA | 0 | 0 | Redacted | MW
Coquille | 115-20.8 kV | 2 | 3 | Coquille | Coquille | Coos | N | N | 4C43 | 5 | MW | 8.784 | MVA | 0 | 0 | 1.75 | MW
Empire | 115-20.8 kV | 1 | 3 | Coos Bay | Coos Bay | Coos | N | N | 4C108 | 3 | MW | 8.78 | MVA | 0.85443 | 0 | 1.05 | MW
Cleveland Ave | 69-12.5kV | 2 | 6 | Bend | Bend | Deschutes | N | N | 5D30 | 5.5 | MW | 10.3 | MVA | 0.15112 | 0 | 1.8 | MW
Cleveland Ave | 69-12.5kV | 2 | 6 | Bend | Bend | Deschutes | N | N | 5D35 | 6.7 | MW | 9.6 | MVA | 0.06239 | 0 | 2 | MW
Cleveland Ave | 69-12.5kV | 2 | 6 | Bend | Bend | Deschutes | N | N | 5D38 | 4 | MW | 9.6 | MVA | 0.12716 | 0 | 1.2876 | MW
Cleveland Ave | 69-12.5kV | 2 | 6 | Bend | Bend | Deschutes | N | N | 5D94 | 8 | MW | 10.3 | MVA | 0.23695 | 0 | 2.3905 | MW
Cleveland Ave | 69-12.5kV | 2 | 6 | Bend | Bend | Deschutes | N | N | 5D96 | 4.2 | MW | 10.3 | MVA | 0.06872 | 0 | 1.1 | MW
Cleveland Ave | 69-12.5kV | 2 | 6 | Bend | Bend | Deschutes | N | N | 5D98 | 5.4 | MW | 10.3 | MVA | 0.05894 | 0 | 1.7 | MW
Empire | 115-20.8 kV | 1 | 3 | Coos Bay | Coos Bay | Coos | N | N | 4C89 | 5.5 | MW | 8.78 | MVA | 0.00315 | 0 | 1.925 | MW
Empire | 115-20.8 kV | 1 | 3 | Coos Bay | Coos Bay | Coos | N | N | 4C90 | 7.188 | MW | 11.916 | MVA | 0.08117 | 0 | 2.5158 | MW
Jordan Point | 115-12.5 kV | 1 | 2 | North Bend | North Bend | Coos | N | N | 5C6 | 3.1 | MW | 7.149 | MVA | 0 | 0 | 1.085 | MW
Coburg | 69-20.8kV | 1 | 1 | Junction City | Albany/Corvallis/Stayton | Lane | N | N | 4M220 | 2.31 | MW | 10 | MVA | 0.06335 | 0 | 0.77665 | MW
Columbia | 115-12.5 kV | 2 | 6 | Portland | Portland | Multnomah | Y | N | 5P266 | 4.9 | MW | 10.3 | MVA | 0.21869 | 0 | 1.7195 | MW
Columbia | 115-12.5 kV | 2 | 6 | Portland | Portland | Multnomah | Y | N | 5P268 | 7.9 | MW | 8.9 | MVA | 0.0099 | 0 | 2.0615 | MW
Columbia | 115-12.5 kV | 2 | 6 | Portland | Portland | Multnomah | Y | N | 5P474 | 5.9 | MW | 8.9 | MVA | 0.00343 | 0 | 1.7765 | MW
Columbia | 115-12.5 kV | 2 | 6 | Portland | Portland | Multnomah | Y | N | 5P476 | 7.3 | MW | 10.3 | MVA | 0.08571 | 0 | 2.4795 | MW
Columbia | 115-12.5 kV | 2 | 6 | Portland | Portland | Multnomah | Y | N | 5P478 | 5.9 | MW | 8.9 | MVA | 0.24426 | 0 | 2.1185 | MW
Columbia | 115-12.5 kV | 2 | 6 | Portland | Portland | Multnomah | Y | Y | 5P480 | Redacted | MW | 8.4 | MVA | 0 | 0 | Redacted | MW
Lockhart | 115-12.5 kV | 2 | 5 | Coos Bay | Coos Bay | Coos | N | N | 4C49 | 1.75 | MW | 7.704 | MVA | 0.01507 | 0 | 0.6125 | MW
Lockhart | 115-12.5 kV | 2 | 5 | Coos Bay | Coos Bay | Coos | N | N | 4C5 | 0.5 | MW | 16 | MVA | 0 | 0 | 0.175 | MW
Lockhart | 115-12.5 kV | 2 | 5 | Coos Bay | Coos Bay | Coos | Y | N | 4C50 | 5 | MW | 8.78 | MVA | 0.02673 | 0 | 2.1483 | MW
Lockhart | 115-12.5 kV | 2 | 5 | Coos Bay | Coos Bay | Coos | N | N | 4C48 | 9.63 | MW | 11.9 | MVA | 0.18816 | 0 | 3.3705 | MW
Crooked River | 69-20.8kV | 2 | 2 | Madras | Madras | Jefferson | N | N | 4D131 | 5 | MW | 13.1 | MVA | 0.38835 | 0 | 1.4661 | MW
Crooked River | 69-20.8kV | 2 | 2 | Madras | Madras | Jefferson | N | N | 4D30 | 2.5 | MW | 11.9 | MVA | 0.17068 | 0 | 0.77839 | MW
Crow Foot | 115-21.8kV | 1 | 2 | Willamette | Albany/Corvallis/Stayton | Linn | N | N | 4M204 | 8.47 | MW | 15.9 | MVA | 0.06669 | 0 | 2.1433 | MW
Crow Foot | 115-21.8kV | 1 | 2 | Willamette | Albany/Corvallis/Stayton | Linn | N | Y | 4M206 | Redacted | MW | 11.9 | MVA | 0.02385 | 0 | Redacted | MW
Cully | 115-12.5 kV | 1 | 3 | Portland | Portland | Multnomah | Y | N | 5P288 | 3.2 | MW | 10.3 | MVA | 0.08121 | 0 | 1.3 | MW
Cully | 115-12.5 kV | 1 | 3 | Portland | Portland | Multnomah | Y | N | 5P290 | 6.2 | MW | 10.3 | MVA | 0.26297 | 0 | 1.31 | MW
Cully | 115-12.5 kV | 1 | 3 | Portland | Portland | Multnomah | Y | N | 5P292 | 7.5 | MW | 10.3 | MVA | 0.25328 | 0 | 1.64 | MW
Culver | 69-12.5kV | 1 | 1 | Madras | Madras | Jefferson | Y | N | 5D5 | 7.1 | MW | 10.3 | MVA | 3.4637 | 0 | 3.36 | MW
Dairy | 69-12.5 kV | 1 | 2 | Dairy | Dairy | Klamath | Y | N | 5L42 | 3.38 | MW | 12.6 | MVA | 8.168 | 0 | -7.16 | MW
Dairy | 69-12.5 kV | 1 | 2 | Dairy | Dairy | Klamath | Y | N | 5L43 | 6.04 | MW | 12.6 | MVA | 10.4835 | 0 | -9.49 | MW
Dallas | 115-21.8kV | 2 | 4 | Willamette | Dallas/Independence | Polk | N | N | 4M100 | 5.68 | MW | 19.88 | MVA | 2.2083 | 1.5 | 0.4 | MW
Dallas | 115-21.8kV | 2 | 4 | Willamette | Dallas/Independence | Polk | N | N | 4M201 | 13 | MW | 15.96 | MVA | 0.11054 | 2.21 | 3.7795 | MW
Dallas | 115-21.8kV | 2 | 4 | Willamette | Dallas/Independence | Polk | Y | N | 4M202 | 9.43 | MW | 15.96 | MVA | 0.13503 | 0 | 2.02 | MW
Dallas | 115-21.8kV | 2 | 4 | Willamette | Dallas/Independence | Polk | N | N | 4M238 | 8.28 | MW | 15.96 | MVA | 0.2041 | 0 | 1.1559 | MW
Wallowa | 69-12.47 | 1 | 1 | Enterprise | Enterprise | Wallowa | N | N | 5W28 | 2.3 | MW |  | MVA | 0.44462 | 1 | -0.44462 | MW
Arlington | 69-12.47 kV | 1 | 1 | Hermiston | Hermiston | Gilliam | N | N | 5K25 | 1.2 | MW | 3.1 | MVA | 0.12246 | 0 | 0.17754 | MW
Blalock | 69-12.47 kV | 1 | 1 | Hermiston | Hermiston | Gilliam | N | N | 5K40 | 0.1 | MW | 0.9 | MVA | 0 | 0 | 0 | MW
Deschutes | 69-12.5kV | 1 | 2 | Redmond | Bend | Deschutes | Y | N | 5D184 | 3.4 | MW | 10.3 | MVA | 15.1211 | 0 | -8.1 | MW
Deschutes | 69-12.5kV | 1 | 2 | Redmond | Bend | Deschutes | Y | N | 5D2 | 3.3 | MW | 9.6 | MVA | 0.33362 | 0 | 1.5 | MVA
Devils Lake | 115-20.8kV | 2 | 4 | Lincoln City | Lincoln City | Lincoln | Y | N | 4A310 | 5.14 | MW | 16 | MVA | 0.06989 | 0 | 2.69 | MW
Devils Lake | 115-20.8kV | 2 | 4 | Lincoln City | Lincoln City | Lincoln | Y | N | 4A312 | 11.71 | MW | 15.4 | MVA | 0.01905 | 0 | 5.33 | MW
Devils Lake | 115-20.8kV | 2 | 4 | Lincoln City | Lincoln City | Lincoln | Y | N | 4A316 | 12.46 | MW | 16 | MVA | 0.11253 | 0 | 3.83 | MW
Devils Lake | 115-20.8kV | 2 | 4 | Lincoln City | Lincoln City | Lincoln | Y | N | 4A338 | 4.07 | MW | 15.4 | MVA | 0 | 0 | 1.6 | MW
Dixon | 115-4kV | 1 | 2 | Willamette | Albany/Corvallis/Stayton | Linn | N | N | 7M26 | 1.73 | MW | 3.7 | MVA | 0.03202 | 0 | 0.49798 | MW
Dixon | 115-4kV | 1 | 2 | Willamette | Albany/Corvallis/Stayton | Linn | N | N | 7M29 | 1.94 | MW | 3.7 | MVA | 0.08597 | 0 | 0.54403 | MW
Dodge Bridge | 69-20.8 | 2 | 2 | Medford | Medford | Jackson | Y | N | 4R1 | 5.6 | MW | 13.1 | MVA | 0.87361 | 10 | 1 | MW
Dodge Bridge | 69-20.8 | 2 | 2 | Medford | Medford | Jackson | N | N | 4R35 | 5.1 | MW | 13.1 | MVA | 0.17234 | 0 | 1.2696 | MW
Dowell | 115-12.5 kV | 1 | 2 | Medford | Grants Pass | Jackson | Y | N | 5R331 | 6.6 | MW | 10.3 | MVA | 0.08662 | 0 | 2.2 | MW
Dowell | 115-12.5 kV | 1 | 2 | Medford | Grants Pass | Jackson | Y | N | 5R334 | 8.9 | MW | 10.3 | MVA | 0.03039 | 0 | 2.3 | MW
Easy Valley | 115-12.5 kV | 2 | 3 | Medford | Grants Pass | Jackson | N | N | 5R123 | 7.1 | MW | 10.3 | MVA | 0.09162 | 0 | 1.371 | MW
Easy Valley | 115-12.5 kV | 2 | 3 | Medford | Grants Pass | Jackson | Y | N | 5R125 | 6 | MW | 10.3 | MVA | 0.08468 | 0 | 1.4 | MW
Easy Valley | 115-12.5 kV | 2 | 3 | Medford | Grants Pass | Jackson | N | N | 5R259 | No Read | MW | 10.3 | MVA | 0.20368 | 0 | 0.6 | MW
Lockhart | 115-12.5 kV | 2 | 5 | Coos Bay | Coos Bay | Coos | N | N | 4C97 | 1.8 | MW | 8.78 | MVA | 0.01644 | 0 | 0.63 | MW
Myrtle Point | 115-20.8 kV | 1 | 2 | Myrtle Point | Myrtle Point | Coos | N | N | 4C36 | 0.878 | MW | 7.704 | MVA | 0.0036 | 0 | 0.3073 | MW
Myrtle Point | 115-20.8 kV | 1 | 2 | Myrtle Point | Myrtle Point | Coos | N | N | 4C37 | 3.63 | MW | 8.78 | MVA | 0.11814 | 0 | 1.2705 | MW
Dalreed | 230-34.5 kV | 4 | 3 | Hermiston | Hermiston | Morrow | Y | N | 4K46 | 14.5 | MW | 21 | MVA | 4.8 | 0 | -1.8 | MW
Dalreed | 230-34.5 kV | 4 | 3 | Hermiston | Hermiston | Morrow | Y | N | 4K36 | 16.9 | MW | 26.3 | MVA | 9.9 | 0 | -9.6 | MW
Dalreed | 230-34.5 kV | 4 | 3 | Hermiston | Hermiston | Morrow | Y | Y | 4K16 | Redacted | MW | 26.4 | MVA | 0 | 0 | Redacted | MW
Fern Hill | 115-12.5 kV | 1 | 2 | Fern Hill | Fern Hill | Clatsop | Y | N | 5A51 | 0.75 | MW | 3.4 | MVA | 0 | 0 | 0.08 | MW
Fern Hill | 115-12.5 kV | 1 | 2 | Fern Hill | Fern Hill | Clatsop | Y | N | 5A52 | 1.5 | MW | 2.9 | MVA | 0.0067 | 0 | 0.728 | MW
Fielder Creek | 115-20.8kV | 1 | 2 | Grants Pass | Grants Pass | Jackson | Y | N | 4R33 | 8.6 | MW | 16.2 | MVA | 0.14144 | 0 | 2.6 | MW
Fielder Creek | 115-20.8kV | 1 | 2 | Grants Pass | Grants Pass | Jackson | Y | N | 4R34 | 3.1 | MW | 16.2 | MVA | 0.09349 | 0 | 0.9 | MW
Foothills | 69-12.5 kV | 2 | 3 | Medford | Medford | Jackson | Y | N | 5R38 | 8.5 | MW | 10.3 | MVA | 0.02232 | 0 | 3.6 | MW
Foothills | 69-12.5 kV | 2 | 3 | Medford | Medford | Jackson | Y | N | 5R39 | 5.5 | MW | 10.3 | MVA | 0.11084 | 0 | 1.2 | MW
Fraley | 69-12.5 kV | 1 | 2 | White City | White City | Jackson | N | N | 5R87 | 3.2 | MW | 3.9 | MVA | 0.16609 | 0 | 0.503 | MW
Fraley | 69-12.5 kV | 1 | 2 | White City | White City | Jackson | N | N | 5R88 | 2.1 | MW | 3.9 | MVA | 0.0292 | 0 | 0.5 | MW
South Dunes | 115-12.5 kV | 1 | 1 | Coos Bay | Coos Bay | Coos | N | N | 5C9 | 3.9 | MW | 6.983 | MVA | 0 | 0 | 1.365 | MW
State Street | 115-20.8 kV | 2 | 4 | North Bend | North Bend | Coos | N | N | 4C67 | 4.25 | MW | 8.78 | MVA | 0.03447 | 0 | 1.4875 | MW
Glendale | 230-12.5 kV | 2 | 2 | Medford | Glendale | Jackson | Y | N | 5R133 | 4.3 | MW | 10.3 | MVA | 1.4289 | 1 | 0 | MW
Glendale | 230-12.5 kV | 2 | 2 | Medford | Glendale | Jackson | Y | N | 5R143 | 6.7 | MW | 10.3 | MVA | 0.0112 | 0 | 1.6 | MW
Gleneden | 20-4kV | 1 | 2 | Lincoln City | Lincoln City | Lincoln | N | N | 7A364 | 1.58 | MW | 3.2 | MVA | 0.0192 | 0 | 0.1308 | MW
Gleneden | 20-4kV | 1 | 2 | Lincoln City | Lincoln City | Lincoln | N | N | 7A366 | 0.78 | MW | 1.8 | MVA | 0 | 0 | 0.09 | MW
State Street | 115-20.8 kV | 2 | 4 | North Bend | North Bend | Coos | N | N | 4C86 | 3.125 | MW | 16 | MVA | 0.15485 | 0 | 1.0938 | MW
State Street | 115-20.8 kV | 2 | 4 | North Bend | North Bend | Coos | N | N | 4C112 | 6.2 | MW | 16 | MVA | 0.11256 | 0 | 2.17 | MW
Gold Hill | 69-12.5 kV | 1 | 1 | Gold Hill | Gold Hill | Jackson | Y | N | 5R103 | 7.6 | MW | 10.3 | MVA | 0.12613 | 0 | 2.7 | MW
Gordon Hollow | 69-20.8 kV | 1 | 1 | Gordon Hollow | Demoss Springs | Sherman | N | N | 4K1 | 3.3 | MW | 7.5 | MVA | 0.06156 | 0 | 0 | MW
Goshen | 115-20.8kV | 1 | 1 | Junction City | Goshen/Village Green | Lane | N | N | 4M360 | 6.18 | MW | 8.78 | MVA | 0.08047 | 1.728 | 0.35153 | MW
Grant | 115-21.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Benton | N | N | 4M265 | 5.53 | MW | 13.9 | MVA | 0.34083 | 0 | 0.50917 | MW
Grant | 115-21.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Benton | N | N | 4M266 | 9 | MW | 15.9 | MVA | 0.24823 | 0 | 3.1018 | MW
Grant | 115-21.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Benton | Y | N | 4M268 | 6 | MW | 15.9 | MVA | 0.39005 | 0 | 1.94 | MW
Grant | 115-21.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Benton | Y | N | 4M269 | 6.19 | MW | 15.9 | MVA | 0.77697 | 0 | 1.66 | MW
State Street | 115-20.8 kV | 2 | 4 | North Bend | North Bend | Coos | N | N | 4C66 | 7 | MW | 11.916 | MVA | 0.10598 | 0 | 2.45 | MW
Canyonville | 115-12.5 kV | 1 | 2 | Canyonville | Canyonville | Douglas | Y | N | 5U46 | 4.6 | MW | 9.353 | MVA | 0.02941 | 0 | 1.6559 | MW
Griffin Creek | 115-12.5 kV | 1 | 2 | Medford | Medford | Jackson | N | N | 5R204 | 8.4 | MW | 10.3 | MVA | 0.0869 | 0 | 1.6627 | MW
Griffin Creek | 115-12.5 kV | 1 | 2 | Medford | Medford | Jackson | N | N | 5R206 | 6.9 | MW | 10.3 | MVA | 0.3146 | 0 | 1.4591 | MW
Hamaker | 69-12.5 kV | 1 | 2 | Keno | Keno | Klamath | N | N | 5L55 | 4.4 | MW | 7.5 | MVA | 0.32052 | 0.978 | 1.0795 | MW
Hamaker | 69-12.5 kV | 1 | 2 | Keno | Keno | Klamath | N | N | 5L56 | 0.44 | MW | 5.1 | MVA | 0 | 0 | 0.154 | MW
Harrisburg | 69-20.8kV | 1 | 1 | Junction City | Albany/Corvallis/Stayton | Linn | N | N | 4M400 | 8.37 | MW | 12.5 | MVA | 0.12209 | 0 | 2.2579 | MW
Hazelwood | 12.5-20.8kV | 1 | 2 | Willamette | Hazelwood | Linn | N | N | 4M335 | 6 | MW | 12.5 | MVA | 0.18141 | 0 | 1.2386 | MW
Hazelwood | 12.5-20.8kV | 1 | 2 | Willamette | Hazelwood | Linn | Y | N | 4M336 | 5.7 | MW | 12.5 | MVA | 0.15083 | 0 | 0.59 | MW
Henley | 69-12.5 kV | 1 | 2 | Klamath Falls | Klamath Falls | Klamath | N | N | 5L58 | 0.907 | MW | 5.8 | MVA | 0.03006 | 3 | -2.8418 | MW
Henley | 69-12.5 kV | 1 | 2 | Klamath Falls | Klamath Falls | Klamath | N | N | 5L59 | 1.858 | MW | 5.8 | MVA | 0.16704 | 0 | 0.06326 | MW
Hermiston | 69-12.47 kV | 1 | 1 | Hermiston | Hermiston | Umatilla | N | N | 5W602 | 6 | MW | 9.2 | MVA | 0.04469 | 0 | 1.4553 | MW
Hillview | 115-20.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Benton | N | N | 4M180 | 5.74 | MW | 15.9 | MVA | 0.53634 | 0 | 0.08366 | MW
Hillview | 115-20.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Benton | N | N | 4M181 | 4.45 | MW | 11.9 | MVA | 0.10856 | 0 | 1.6514 | MW
Hillview | 115-20.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Benton | Y | N | 4M182 | 14.47 | MW | 26.25 | MVA | 8.0811 | 0.897 | 1.743 | MW
Hillview | 115-20.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Benton | N | N | 4M185 | 6.64 | MW | 11.9 | MVA | 0.42617 | 0 | 2.1538 | MW
Hinkle | 69-12.47 kV | 1 | 1 | Hermiston | Hermiston | Umatilla | N | N | 5W82 | 3.8 | MW | 9.6 | MVA | 0.94281 | 0 | 0.35719 | MW
Holladay | 115-11.7 kV | 3 | 6 | Portland | Portland | Multnomah | Y | Y | 5P145 | Redacted | MW | 9.43 | MVA | 0 | 0 | Redacted | MW
Holladay | 115-11.7 kV | 3 | 6 | Portland | Portland | Multnomah | Y | Y | 5P146 | Redacted | MW | 9.43 | MVA | 0 | 0 | Redacted | MW
Holladay | 115-11.7 kV | 3 | 6 | Portland | Portland | Multnomah | Y | Y | 5P147 | Redacted | MW | 9.43 | MVA | 0 | 0 | Redacted | MW
Holladay | 115-11.7 kV | 3 | 6 | Portland | Portland | Multnomah | Y | N | 5P156 | 5.41 | MW | 9.3 | MVA | 0 | 0 | 1.81 | MW
Holladay | 115-11.7 kV | 3 | 6 | Portland | Portland | Multnomah | Y | N | 5P157 | 6.48 | MW | 10.1 | MVA | 1.9984 | 0 | 1.12 | MW
Holladay | 115-11.7 kV | 3 | 6 | Portland | Portland | Multnomah | Y | N | 5P158 | 6.59 | MW | 10.3 | MVA | 0.09533 | 0 | 2.47 | MW
Hollywood | 115-12.5 kV | 2 | 5 | Portland | Portland | Multnomah | N | N | 5P203 | 6.9 | MW | 9.5 | MVA | 0.15707 | 0 | 1.7679 | MW
Hollywood | 115-12.5 kV | 2 | 5 | Portland | Portland | Multnomah | N | N | 5P204 | 3.2 | MW | 9.5 | MVA | 0.12547 | 0 | 0.64453 | MW
Hollywood | 115-12.5 kV | 2 | 5 | Portland | Portland | Multnomah | N | N | 5P205 | 6 | MW | 9.5 | MVA | 0.1947 | 0 | 0.1553 | MW
Hollywood | 115-12.5 kV | 2 | 5 | Portland | Portland | Multnomah | N | N | 5P208 | 8 | MW | 10.3 | MVA | 0.49522 | 0 | 1.4298 | MW
Hollywood | 115-12.5 kV | 2 | 5 | Portland | Portland | Multnomah | N | N | 5P209 | 5 | MW | 10.3 | MVA | 0.14834 | 0 | 1.4267 | MW
Hood River | 69-12.5 kV | 2 | 5 | Hood River | Hood River | Hood River | N | N | 5K43 | 3.2 | MW | 5.3 | MVA | 0.48092 | 0 | 0.06608 | MW
Hood River | 69-12.5 kV | 2 | 5 | Hood River | Hood River | Hood River | N | N | 5K37 | 7.83 | MW | 10.3 | MVA | 0.48342 | 0 | 1.0106 | MW
Hood River | 69-12.5 kV | 2 | 5 | Hood River | Hood River | Hood River | Y | N | 5K74 | 6 | MW | 6.8 | MVA | 0.92464 | 0 | 1.7 | MW
Hood River | 69-12.5 kV | 2 | 5 | Hood River | Hood River | Hood River | Y | N | 5K70 | 4.5 | MW | 8.5 | MVA | 0.34024 | 0 | 1.1 | MW
Hood River | 69-12.5 kV | 2 | 5 | Hood River | Hood River | Hood River | N | N | 5K44 | 7.8 | MW | 9.6 | MVA | 0.58242 | 0 | 1.1876 | MW
Hornet | 69-12.5 kV | 1 | 2 | Klamath Falls | Klamath Falls | Klamath | N | N | 5K50 | 2.3 | MW | 4.5 | MVA | 0.24138 | 0 | 0.05186 | MW
Hornet | 69-12.5 kV | 1 | 2 | Klamath Falls | Klamath Falls | Klamath | Y | N | 5L45 | 4.74 | MW | 10.08 | MVA | 2.4234 | 1.125 | 1.4 | MW
Humburg Creek | 69-12.5 kV | 1 | 1 | Medford | Medford | Jackson | N | N | 5R287 | 3.1 | MW | 9.4 | MVA | 0.16497 | 0 | 0.49196 | MW
Hunters Circle | 69-12.5kV | 1 | 1 | Bend | Bend | Deschutes | N | N | 5D192 | 3 | MW | 10.3 | MVA | 0.13104 | 0 | 1 | MW
Canyonville | 115-12.5 kV | 1 | 2 | Canyonville | Canyonville | Douglas | Y | N | 5U52 | 2.5 | MW | 8.78 | MVA | 0.02916 | 0 | 1 | MW
Independence | 69-21.8kV | 1 | 2 | Willamette | Dallas/Independence | Polk | N | N | 4M22 | 13.5 | MW | 27.24 | MVA | 0.55467 | 6 | 4.8 | MW
Independence | 69-21.8kV | 1 | 2 | Willamette | Dallas/Independence | Polk | N | N | 4M25 | 7.6 | MW | 11.9 | MVA | 0.27998 | 0 | 2.36 | MW
Jacksonville | 115-12.5 kV | 1 | 2 | Jacksonville | Jacksonville | Jackson | Y | N | 5R284 | 8.1 | MW | 10.3 | MVA | 0.30882 | 0 | 2.4 | MW
Jacksonville | 115-12.5 kV | 1 | 2 | Jacksonville | Jacksonville | Jackson | Y | N | 5R285 | 8.4 | MW | 10.3 | MVA | 0.72221 | 1.125 | 2.1 | MW
Jefferson | 69-20.8kV | 1 | 2 | Willamette | Albany/Corvallis/Stayton | Linn | Y | N | 4M117 | 3.08 | MW | 11.9 | MVA | 0.09136 | 0 | 0.83 | MW
Jefferson | 69-20.8kV | 1 | 2 | Willamette | Albany/Corvallis/Stayton | Linn | N | N | 4M125 | 8.49 | MW | 11.9 | MVA | 0.30411 | 0 | 2.8759 | MW
Jerome Prairie | 115-12.5 kV | 1 | 2 | Medford | Grants Pass | Jackson | Y | N | 5R62 | 5.3 | MW | 9.5 | MVA | 0.19125 | 0 | 1.9 | MW
Jerome Prairie | 115-12.5 kV | 1 | 2 | Medford | Grants Pass | Jackson | Y | N | 5R63 | 6.5 | MW | 9.5 | MVA | 0.14671 | 0 | 2 | MW
Carnes | 69-12.5 kV | 1 | 1 | Winston | Winston | Douglas | N | N | 5U44 | 1.5 | MW | 8.78 | MVA | 0 | 0 | 0.54049 | MW
Umatilla | 69-12.47 kV | 2 | 3 | Hermiston | Hermiston | Umatilla | Y | N | 5W658 | 5.7 | MW | 10.3 | MVA | 0.00858 | 0 | 1.6 | MW
Junction City | 69-20.8kV | 2 | 2 | Junction City | Albany/Corvallis/Stayton | Lane | N | N | 4M102 | 5.87 | MW | 12.5 | MVA | 0.33297 | 0 | 1.657 | MW
Junction City | 69-20.8kV | 2 | 2 | Junction City | Albany/Corvallis/Stayton | Lane | N | N | 4M99 | 3.28 | MW | 9.38 | MVA | 0.00512 | 0 | 1.0349 | MW
Kenwood | 69-12.5 kV | 1 | 1 | Hood River | Hood River | Hood River | N | N | 5K50 | 2.3 | MW | 4.5 | MVA | 0.24138 | 0 | 0.22062 | MW
Killingsworth | 69-12.5 kV | 2 | 5 | Portland | Portland | Multnomah | Y | N | 5P123 | 2.4 | MW | 9.8 | MVA | 0.02632 | 0 | 0.32 | MW
Killingsworth | 69-12.5 kV | 2 | 5 | Portland | Portland | Multnomah | Y | N | 5P217 | 6.2 | MW | 9.5 | MVA | 0.1259 | 0 | 1.76 | MW
Killingsworth | 69-12.5 kV | 2 | 5 | Portland | Portland | Multnomah | Y | N | 5P41 | 7.5 | MW | 8.7 | MVA | 0.32255 | 0 | 2.24 | MW
Killingsworth | 69-12.5 kV | 2 | 5 | Portland | Portland | Multnomah | Y | Y | 5P88 | Redacted | MW | 9.5 | MVA | 0 | 0 | Redacted | MW
Killingsworth | 69-12.5 kV | 2 | 5 | Portland | Portland | Multnomah | Y | N | 5P89 | 6.5 | MW | 9.5 | MVA | 0.4419 | 0 | 2.08 | MW
Knappa Svensen | 115-12.5 kV | 1 | 2 | Knappa Svensen | Knappa Svensen | Clatsop | Y | N | 5A92 | 1.31 | MW | 7.1 | MVA | 0.04012 | 0 | 0.22 | MW
Knappa Svensen | 115-12.5 kV | 1 | 2 | Knappa Svensen | Knappa Svensen | Clatsop | Y | N | 5A93 | 0.75 | MW | 4.5 | MVA | 0.03668 | 0 | 0.195 | MW
Knott | 115-12.5 kV | 2 | 7 | Portland | Portland | Multnomah | Y | N | 5P231 | 0.6 | MW | 10.3 | MVA | 0.0167 | 0 | 0.209 | MW
Knott | 115-12.5 kV | 2 | 7 | Portland | Portland | Multnomah | Y | N | 5P232 | 8.2 | MW | 10.3 | MVA | 0.2956 | 0 | 3.47 | MW
Knott | 115-12.5 kV | 2 | 7 | Portland | Portland | Multnomah | Y | N | 5P233 | 5.6 | MW | 10.3 | MVA | 0.13577 | 0 | 1.78 | MW
Knott | 115-11.7 kV | 2 | 7 | Portland | Portland | Multnomah | Y | N | 5P366 | 2.9 | MW | 10.3 | MVA | 0 | 0 | 0.978 | MW
Knott | 115-11.7 kV | 2 | 7 | Portland | Portland | Multnomah | Y | N | 5P368 | 5.8 | MW | 10.3 | MVA | 0.0168 | 0 | 0.766 | MW
Knott | 115-11.7 kV | 2 | 7 | Portland | Portland | Multnomah | Y | N | 5P372 | 4.9 | MW | 10.3 | MVA | 0 | 0 | 1.52 | MW
Knott | 115-11.7 kV | 2 | 7 | Portland | Portland | Multnomah | Y | N | 5P374 | 3.4 | MW | 10.3 | MVA | 0.01293 | 0 | 1.12 | MW
Lakeport | 69-12.5 kV | 2 | 3 | Klamath Falls | Klamath Falls | Klamath | Y | N | 5L49 | 5.75 | MW | 12.59 | MVA | 4.3292 | 0 | 1.391 | MW
Lakeport | 69-12.5 kV | 2 | 3 | Klamath Falls | Klamath Falls | Klamath | Y | N | 5L54 | 5.47 | MW | 10.08 | MVA | 0.18051 | 0 | 2.508 | MW
Lakeport | 69-12.5 kV | 2 | 3 | Klamath Falls | Klamath Falls | Klamath | Y | Y | 5L61 | Redacted | MW | 5.2 | MVA | 0 | 0 | Redacted | MW
Lancaster | 69-20.8kV | 1 | 1 | Junction City | Albany/Corvallis/Stayton | Lane | N | N | 4M209 | 8.55 | MW | 9.1 | MVA | 0.08065 | 0 | 0.95935 | MW
Lebanon | 115-20.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Linn | Y | N | 4M61 | 7.77 | MW | 11.3 | MVA | 0.11253 | 0 | 3.23 | MW
Lebanon | 115-20.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Linn | N | N | 4M62 | 9.6 | MW | 11.3 | MVA | 0.0415 | 0 | 2.9685 | MW
Lebanon | 115-20.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Linn | N | N | 4M63 | 5 | MW | 11.3 | MVA | 1.2141 | 0 | 0.69592 | MW
Lebanon | 115-20.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Linn | N | Y | 4M79 | Redacted | MW | 19.1 | MVA | 0.2068 | 0 | Redacted | MW
Clearwater #1 | 115-12.5 kV | 1 | 1 | Idleyld Park | Idleyld Park | Douglas | N | N | 6U17 | 0.06 | MW | 0.1 | MVA | 0 | 0 | 0.021 | MW
Lincoln | 115-11.7 kV | 3 | 15 | Portland | Portland | Multnomah | Y | Y | 5P418 | Redacted | MW | 9.6 | MVA | 0 | 0 | Redacted | MW
Lincoln | 115-11.7 kV | 3 | 15 | Portland | Portland | Multnomah | Y | Y | 5P420 | Redacted | MW | 9.6 | MVA | 0.022 | 0 | Redacted | MW
Lincoln | 115-11.7 kV | 3 | 15 | Portland | Portland | Multnomah | Y | N | 5P422 | 3.1 | MW | 10.2 | MVA | 0.00975 | 0 | 1.03 | MW
Lincoln | 115-11.7 kV | 3 | 15 | Portland | Portland | Multnomah | Y | Y | 5P424 | Redacted | MW | 10.2 | MVA | 0 | 0 | Redacted | MW
Lincoln | 115-11.7 kV | 3 | 15 | Portland | Portland | Multnomah | Y | N | 5P426 | 3.7 | MW | 10.2 | MVA | 0 | 0 | 0.405 | MW
Lincoln | 115-11.7 kV | 3 | 15 | Portland | Portland | Multnomah | Y | N | 5P430 | 2.6 | MW | 10.2 | MVA | 0.0495 | 0 | 0.632 | MW
Lincoln | 115-11.7 kV | 3 | 15 | Portland | Portland | Multnomah | Y | N | 5P432 | 4.7 | MW | 10.2 | MVA | 0 | 0 | 1.932 | MW
Lincoln | 115-11.7 kV | 3 | 15 | Portland | Portland | Multnomah | Y | Y | 5P434 | Redacted | MW | 10.2 | MVA | 0 | 0 | Redacted | MW
Lincoln | 115-11.7 kV | 3 | 15 | Portland | Portland | Multnomah | Y | Y | 5P436 | Redacted | MW | 9.6 | MVA | 0 | 0 | Redacted | MW
Lincoln | 115-11.7 kV | 3 | 15 | Portland | Portland | Multnomah | Y | Y | 5P438 | Redacted | MW | 9.6 | MVA | 0 | 0 | Redacted | MW
Lincoln | 115-11.7 kV | 3 | 15 | Portland | Portland | Multnomah | Y | Y | 5P456 | Redacted | MW | 9.6 | MVA | 0 | 0 | Redacted | MW
Lincoln | 115-11.7 kV | 3 | 15 | Portland | Portland | Multnomah | Y | N | 5P458 | 2.2 | MW | 10.2 | MVA | 0 | 0 | 0.611 | MW
Lincoln | 115-11.7 kV | 3 | 15 | Portland | Portland | Multnomah | Y | Y | 5P460 | Redacted | MW | 10.2 | MVA | 0 | 0 | Redacted | MW
Lincoln | 115-11.7 kV | 3 | 15 | Portland | Portland | Multnomah | Y | Y | 5P462 | Redacted | MW | 9.6 | MVA | 0 | 0 | Redacted | MW
Lincoln | 115-11.7 kV | 3 | 15 | Portland | Portland | Multnomah | Y | Y | 5P464 | Redacted | MW | 9.6 | MVA | 0 | 0 | Redacted | MW
Clearwater #2 | 115-12.5 kV | 1 | 1 | Idleyld Park | Idleyld Park | Douglas | Y | N | 6U33 | 0.25 | MW | 0.5 | MVA | 0.04589 | 0 | 0.025 | MW
Cloake | 69-12.5 kV | 1 | 3 | Roseburg | Roseburg | Douglas | Y | Y | 4U37 | Redacted | MW | 7.56 | MVA | 0 | 0 | Redacted | MW
Cloake | 69-12.5 kV | 1 | 3 | Roseburg | Roseburg | Douglas | Y | N | 4U38 | 9.8 | MW | 11.916 | MVA | 0.07056 | 0 | 2.882 | MW
Cloake | 69-12.5 kV | 1 | 3 | Roseburg | Roseburg | Douglas | Y | N | 4U39 | 4.3 | MW | 11.916 | MVA | 0.10601 | 0 | 0.816 | MW
Garden Valley | 69-20.8 kV | 1 | 2 | Roseburg | Roseburg | Douglas | N | N | 4U80 | 5.65 | MW | 8.64 | MVA | 0.014 | 0 | 1.9775 | MW
Lyons | 69-20.8kV | 2 | 2 | Willamette | Lyons/Scio | Linn | Y | N | 4M120 | 10.92 | MW | 12.5 | MVA | 0.05225 | 1.5 | 2 | MW
Lyons | 69-20.8kV | 2 | 2 | Willamette | Lyons/Scio | Linn | Y | N | 4M70 | 10.68 | MW | 12.5 | MVA | 0.06603 | 0 | 3.2 | MW
Madras | 69-12.5kV | 2 | 4 | Madras | Madras | Jefferson | Y | N | 5D52 | 3.3 | MW | 10.3 | MVA | 10.157 | 0 | -8.7 | MW
Madras | 69-12.5kV | 2 | 4 | Madras | Madras | Jefferson | N | N | 5D57 | 5 | MW | 10.3 | MVA | 0.08257 | 0 | 1.5 | MW
Madras | 69-12.5kV | 2 | 4 | Madras | Madras | Jefferson | N | N | 5D53 | 8.1 | MW | 10.3 | MVA | 0.09821 | 0 | 1.897 | MW
Madras | 69-12.5kV | 2 | 4 | Madras | Madras | Jefferson | N | N | 5D61 | 4.9 | MW | 9.5 | MVA | 0.07148 | 0 | 1.3 | MW
Mallory | 115-12.5 kV | 1 | 3 | Portland | Portland | Multnomah | Y | N | 5P162 | 4.3 | MW | 10.3 | MVA | 0.14499 | 0 | 1.46 | MW
Mallory | 115-12.5 kV | 1 | 3 | Portland | Portland | Multnomah | Y | N | 5P164 | 8.7 | MW | 10.3 | MVA | 0.4072 | 0 | 2.57 | MW
Mallory | 115-12.5 kV | 1 | 3 | Portland | Portland | Multnomah | N/A | N | 5P166 | N/A | MW | 10.3 | MVA | 0 | 0 | N/A | MW
Marys River | 115-20.8kV | 1 | 3 | Willamette | Albany/Corvallis/Stayton | Benton | N | N | 4M151 | 10.6 | MW | 21 | MVA | 0.90466 | 0 | 3.2153 | MW
Marys River | 115-20.8kV | 1 | 3 | Willamette | Albany/Corvallis/Stayton | Benton | N | N | 4M152 | 2.1 | MW | 21 | MVA | 0.01853 | 0 | 0.87147 | MW
Marys River | 115-20.8kV | 1 | 3 | Willamette | Albany/Corvallis/Stayton | Benton | N | N | 4M153 | 4.8 | MW | 11.9 | MVA | 0 | 0 | 3.14 | MW
Medco | 115-12.5 kV | 1 | 1 | Medford | Medford | Jackson | N | Y | 5R280 | Redacted | MW | 20 | MVA | 0 | 0 | Redacted | MW
Medford | 69-12.5 kV | 2 | 2 | Medford | Medford | Jackson | N | N | 5R21 | 5.3 | MW | 8.3 | MVA | 0.01592 | 0 | 0.98408 | MW
Medford | 69-12.5 kV | 2 | 2 | Medford | Medford | Jackson | N | N | 5R23 | 5.9 | MW | 8.3 | MVA | 0.03032 | 0 | 1.1889 | MW
Merlin | 115-12.5 kV | 2 | 5 | Grants Pass | Merlin | Jackson | Y | N | 5R232 | 8.6 | MW | 10.3 | MVA | 0.06918 | 0 | 0.5 | MW
Merlin | 115-12.5 kV | 2 | 5 | Grants Pass | Merlin | Jackson | Y | N | 5R234 | 5.6 | MW | 10.3 | MVA | 0.22667 | 0 | 2.1 | MW
Merlin | 115-12.5 kV | 2 | 5 | Grants Pass | Merlin | Jackson | Y | N | 5R248 | 6.3 | MW | 10.3 | MVA | 0.0479 | 0 | 1.2 | MW
Merlin | 115-12.5 kV | 2 | 5 | Grants Pass | Merlin | Jackson | Y | N | 5R251 | 3.4 | MW | 10.3 | MVA | 0.12014 | 0 | 1.1 | MW
Merrill | 69-12.5 kV | 2 | 2 | Merrill | Merrill | Klamath | Y | N | 5L26 | 4.78 | MW | 8.6 | MVA | 0.33835 | 0.8 | 0.37 | MW
Merrill | 69-12.5 kV | 2 | 2 | Merrill | Merrill | Klamath | Y | N | 5L27 | 3.73 | MW | 8.6 | MVA | 8.2968 | 0 | -7.46 | MW
Mile Hi | 115-12.5 kV | 1 | 2 | Lakeview | Lakeview | Lake | Y | N | 5L104 | 4.93 | MW | 11.3 | MVA | 10.0303 | 0 | -8.39 | MW
Mile Hi | 115-12.5 kV | 1 | 2 | Lakeview | Lakeview | Lake | Y | N | 5L105 | 5.05 | MW | 9.4 | MVA | 10.8727 | 0 | -8.53 | MW
Umatilla | 69-12.47 kV | 2 | 3 | Hermiston | Hermiston | Umatilla | Y | N | 5W660 | 4.3 | MW | 10.3 | MVA | 0.02176 | 0 | 0.9 | MW
Modoc | 69-12.5 kV | 1 | 1 | Chiloquin | Chiloquin | Klamath | N | N | 5L36 | 2.773 | MW | 5.8 | MVA | 0.42625 | 0.8 | 0.97 | MW
Murder Creek | 115-12kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Linn | N | Y | 4M243 | Redacted | MW | 13.9 | MVA | 0.78446 | 2.875 | Redacted | MW
Murder Creek | 115-12kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Linn | N | Y | 4M245 | Redacted | MW | 19.9 | MVA | 0.5799 | 0 | Redacted | MW
Murder Creek | 115-12kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Linn | N | Y | 4M249 | Redacted | MW | 15.9 | MVA | 0.0261 | 0 | Redacted | MW
Murder Creek | 115-12kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Linn | N | Y | 4M250 | Redacted | MW | 19.3 | MVA | 0 | 0 | Redacted | MW
Garden Valley | 69-20.8 kV | 1 | 2 | Roseburg | Roseburg | Douglas | Y | N | 4U81 | 5.9475 | MW | 13.932 | MVA | 0.10862 | 0 | 1.9248 | MW
Glide | 115-12.5 kV | 1 | 2 | Glide | Glide | Douglas | N | N | 5U83 | 2.725 | MW | 11.268 | MVA | 0.10226 | 0 | 0.95375 | MW
Glide | 115-12.5 kV | 1 | 2 | Glide | Glide | Douglas | N | N | 5U84 | 4.147 | MW | 11.268 | MVA | 0.1073 | 0 | 1.4442 | MW
Green | 69-12.5 kV | 2 | 2 | Roseburg | Roseburg | Douglas | Y | N | 5U32 | 5.7435 | MW | 8.043 | MVA | 0.03688 | 0 | 1.7404 | MW
Nelscott | 20-4kV | 1 | 1 | Lincoln City | Lincoln City | Lincoln | N | N | 7A390 | 0.7 | MW | 1.8 | MVA | 0.0018 | 0 | 0.3782 | MW
New Medford | 115-12.5 kV | 2 | 4 | Medford | Medford | Jackson | Y | N | 5R250 | 6.2 | MW | 11.4 | MVA | 0.49517 | 0 | 1.9 | MW
New Medford | 115-12.5 kV | 2 | 4 | Medford | Medford | Jackson | Y | N | 5R253 | 7.2 | MW | 10.3 | MVA | 0.17845 | 0 | 2.6 | MW
New Medford | 115-12.5 kV | 2 | 4 | Medford | Medford | Jackson | Y | N | 5R257 | 7.5 | MW | 10.3 | MVA | 0.12385 | 0 | 1.9 | MW
New Medford | 115-12.5 kV | 2 | 4 | Medford | Medford | Jackson | Y | N | 5R659 | 5.1 | MW | 10.3 | MVA | 0 | 0 | 1.6 | MW
New O'Brien | 115-12.5 kV | 1 | 1 | Medford | Cave Junction | Jackson | Y | N | 5R106 | 1.1 | MW | 9.4 | MVA | 0.0108 | 0 | 0.5 | MW
Oak Knoll | 115-12.5 kV | 2 | 4 | Medford | Medford | Jackson | Y | N | 5R55 | 4.7 | MW | 9.5 | MVA | 0.58406 | 2.999 | 1.5 | MW
Oak Knoll | 115-12.5 kV | 2 | 4 | Medford | Medford | Jackson | Y | Y | 5R56 | Redacted | MW | N/A | MVA | 0.06756 | 0 | Redacted | MW
Oak Knoll | 115-12.5 kV | 2 | 4 | Medford | Medford | Jackson | Y | Y | 5R70 | Redacted | MW | N/A | MVA | 0 | 0 | Redacted | MW
Oak Knoll | 115-12.5 kV | 2 | 4 | Medford | Medford | Jackson | Y | Y | 5R93 | Redacted | MW | N/A | MVA | 0 | 0 | Redacted | MW
Green | 69-12.5 kV | 2 | 2 | Roseburg | Roseburg | Douglas | Y | N | 5U33 | 8.4208 | MW | 11.04 | MVA | 0.50859 | 0 | 2.779 | MW
Illahee Flats | 115-7.2 kV | 1 | 1 | Roseburg | Roseburg | Douglas | N | N | 6U13 | 0.0869 | MW | 1.1168 | MVA | 0 | 0 | 0.030415 | MW
Oremet | 115-12kV | 2 | 2 | Willamette | Albany/Corvallis/Stayton | Linn | N | Y | 4M295 | Redacted | MW | 21.6 | MVA | 0 | 0 | Redacted | MW
Oremet | 115-12kV | 2 | 2 | Willamette | Albany/Corvallis/Stayton | Linn | N | Y | 4M296 | Redacted | MW | 15.9 | MVA | 0.38758 | 0 | Redacted | MW
Overpass | 69-12.5kV | 2 | 5 | Bend | Bend | Deschutes | N | N | 5D104 | 6.4 | MW | 10.3 | MVA | 0.17907 | 0 | 2.2 | MW
Overpass | 69-12.5kV | 2 | 5 | Bend | Bend | Deschutes | N | N | 5D106 | 7.3 | MW | 10.3 | MVA | 0.8344 | 0 | 2.4 | MW
Overpass | 69-12.5kV | 2 | 5 | Bend | Bend | Deschutes | N | N | 5D120 | 9.3 | MW | 10.3 | MVA | 0.33337 | 0 | 2.8 | MW
Overpass | 69-12.5kV | 2 | 5 | Bend | Bend | Deschutes | N | N | 5D128 | 8.4 | MW | 10.3 | MVA | 2.1925 | 0.72 | 2.4 | MW
Overpass | 69-12.5kV | 2 | 5 | Bend | Bend | Deschutes | Y | N | 5D155 | 9.6 | MW | 10.3 | MVA | 0.09245 | 0 | 2 | MW
Umatilla | 69-12.47 kV | 2 | 3 | Hermiston | Hermiston | Umatilla | Y | N | 5W664 | 4 | MW | 10.3 | MVA | 0 | 0 | 0.6 | MW
Athena | 69-12.47 kV | 1 | 2 | Pendleton | Pendleton | Umatilla | N | N | 5W703 | 2.7 | MW | 3.8 | MVA | 0.03299 | 0 | 0.8 | MW
Park Street | 115-12.5 kV | 2 | 5 | Medford | Grants Pass | Jackson | N | N | 5R114 | 9.9 | MW | 10.3 | MVA | 0.0706 | 0 | 0.74 | MW
Park Street | 115-12.5 kV | 2 | 5 | Medford | Grants Pass | Jackson | N | N | 5R115 | 5.5 | MW | 10.3 | MVA | 0.04756 | 0 | 1.3 | MW
Park Street | 115-12.5 kV | 2 | 5 | Medford | Grants Pass | Jackson | N | N | 5R121 | 8.8 | MW | 10.3 | MVA | 0.06286 | 0 | 2.5 | MW
Park Street | 115-12.5 kV | 2 | 5 | Medford | Grants Pass | Jackson | N | N | 5R164 | 4.4 | MW | 10.3 | MVA | 0 | 0 | 1.2 | MW
Park Street | 115-12.5 kV | 2 | 5 | Medford | Grants Pass | Jackson | N | N | 5R169 | 6.9 | MW | 10.3 | MVA | 0.03526 | 0 | 1.7 | MW
Parkrose | 115-12.5 kV | 2 | 4 | Portland | Portland | Multnomah | Y | N | 5P244 | 7.3 | MW | 9.5 | MVA | 0.14331 | 0 | 2.53 | MW
Parkrose | 115-12.5 kV | 2 | 4 | Portland | Portland | Multnomah | Y | N | 5P246 | 7.2 | MW | 9.5 | MVA | 0.10286 | 0 | 2.03 | MW
Parkrose | 115-12.5 kV | 2 | 4 | Portland | Portland | Multnomah | Y | N | 5P250 | 7.2 | MW | 9.5 | MVA | 0.00589 | 0 | 1.21 | MW
Parkrose | 115-12.5 kV | 2 | 4 | Portland | Portland | Multnomah | Y | N | 5P252 | 7.1 | MW | 9.5 | MVA | 0.10948 | 0 | 1.86 | MW
Parkrose | 115-12.5 kV | 2 | 4 | Portland | Portland | Multnomah | Y | N | 5P717 | 5.03 | MW | 10.3 | MVA | 0.056 | 0 | 1.649 | MW
Athena | 69-12.47 kV | 1 | 2 | Pendleton | Pendleton | Umatilla | N | N | 5W705 | 2.9 | MW | 3 | MVA | 0.03047 | 0 | 0.26953 | MW
Buckaroo | 69-12.47 kV | 2 | 3 | Pendleton | Pendleton | Umatilla | Y | N | 5W201 | 4.5 | MW | 9.8 | MVA | 6.4241 | 0 | -3.9 | MW
Buckaroo | 69-12.47 kV | 2 | 3 | Pendleton | Pendleton | Umatilla | Y | N | 5W202 | 9 | MW | 10.3 | MVA | 0.78638 | 0 | 3 | MW
Buckaroo | 69-12.47 kV | 2 | 3 | Pendleton | Pendleton | Umatilla | Y | N | 5W203 | 6.6 | MW | 10.3 | MVA | 0.20892 | 0 | 2.4 | MW
Pendleton | 69-4.16 kV | 6 | 7 | Pendleton | Pendleton | Umatilla | Y | N | 7W451 | 2.2 | MW | 2.6 | MVA | 0.0521 | 0 | 0.3 | MW
Pendleton | 69-4.16 kV | 6 | 7 | Pendleton | Pendleton | Umatilla | Y | N | 7W452 | 1.6 | MW | 2.6 | MVA | 0.04039 | 0 | 0.5 | MW
Pendleton | 69-4.16 kV | 6 | 7 | Pendleton | Pendleton | Umatilla | Y | N | 7W453 | 1.1 | MW | 2.6 | MVA | 0 | 0 | 0.3 | MW
Pilot Butte | 69-12.5kV | 1 | 4 | Bend | Bend | Deschutes | Y | N | 5D261 | 3.6 | MW | 10.3 | MVA | 10.1439 | 0 | -7.3 | MW
Pilot Butte | 69-12.5kV | 1 | 4 | Bend | Bend | Deschutes | Y | N | 5D263 | 5 | MW | 10.3 | MVA | 10.3925 | 0 | -5.6 | MW
Pilot Butte | 69-12.5kV | 1 | 4 | Bend | Bend | Deschutes | Y | N | 5D265 | 3.9 | MW | 10.3 | MVA | 10.0054 | 0 | -7.8 | MW
Pendleton | 69-4.16 kV | 6 | 7 | Pendleton | Pendleton | Umatilla | Y | N | 7W454 | 1.4 | MW | 2.6 | MVA | 0.00648 | 0 | 0.2 | MW
Pendleton | 69-.12.47 kV | 6 | 7 | Pendleton | Pendleton | Umatilla | Y | N | 5W401 | 5.4 | MW | 10.3 | MVA | 0.15551 | 0 | 2.4 | MW
Powell Butte | 115-12.5kV | 1 | 1 | Redmond | Redmond/Prineville | Crook | N | N | 5D1 | 3.4 | MW | 7.2 | MVA | 1.3278 | 0 | 1.6 | MVA
Prineville | 115-12.5kV | 2 | 7 | Redmond | Redmond/Prineville | Crook | N | N | 5D126 | 4 | MW | 10.3 | MVA | 0.05642 | 0.81 | 1.4 | MW
Prineville | 115-12.5kV | 2 | 7 | Redmond | Redmond/Prineville | Crook | Y | N | 5D167 | 8.2 | MW | 10.3 | MVA | 0.16007 | 0 | 3.5 | MW
Prineville | 115-12.5kV | 2 | 7 | Redmond | Redmond/Prineville | Crook | N | N | 5D25 | 7.2 | MW | 10.3 | MVA | 0.46458 | 0 | 1.7 | MW
Prineville | 115-12.5kV | 2 | 7 | Redmond | Redmond/Prineville | Crook | N | N | 5D47 | 5.7 | MW | 9.6 | MVA | 0.18491 | 0 | 1.8 | MW
Prineville | 115-12.5kV | 2 | 7 | Redmond | Redmond/Prineville | Crook | N | N | 5D48 | 3.8 | MW | 10.3 | MVA | 0.0385 | 0 | 1.3 | MW
Prineville | 115-12.5kV | 2 | 7 | Redmond | Redmond/Prineville | Crook | Y | N | 5D50 | 1.7 | MW | 10.3 | MVA | 0 | 0 | 0.7 | MVA
Prineville | 115-12.5kV | 2 | 7 | Redmond | Redmond/Prineville | Crook | N | N | 5D69 | 7.8 | MW | 10.3 | MVA | 0.17125 | 1.46 | 2.7 | MW
Prospect | 69-12.5 kV | 1 | 1 | Prospect | Prospect | Jackson | N | N | 5R40 | 1 | MW | 1.5 | MVA | 0.004 | 0 | 0.3 | MW
Provolt | 69-12.5 kV | 1 | 1 | Grants Pass | Provolt | Jackson | N | N | 5R67 | 6 | MW | 7.8 | MVA | 0.25264 | 0 | 1.7 | MW
Queen Ave | 69-21.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Linn | Y | N | 4M217 | 10.02 | MW | 15.9 | MVA | 0.06201 | 0 | 0.5 | MW
Queen Ave | 69-21.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Linn | N | N | 4M258 | 11 | MW | 21.6 | MVA | 0.44834 | 0 | 4.5417 | MW
Queen Ave | 69-21.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Linn | N | N | 4M261 | 9.9 | MW | 14.4 | MVA | 0.30135 | 0 | 3.0087 | MW
Queen Ave | 69-21.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Linn | N | N | 4M262 | 5.8 | MW | 14.4 | MVA | 0.09796 | 0 | 2.382 | MW
Red Blanket | 69-2.2 kV | 1 | 1 | Prospect | Prospect | Jackson | N | N | 7R5 | 0.9 | MW | 1.5 | MVA | 0 | 0 | 0.2 | MW
Redmond | 115-12.5kV | 2 | 7 | Redmond | Redmond/Prineville | Deschutes | Y | N | 5D21 | 3 | MW | 10.3 | MVA | 0.0621 | 0 | 1.5 | MVA
Redmond | 115-12.5kV | 2 | 7 | Redmond | Redmond/Prineville | Deschutes | Y | N | 5D22 | 5.2 | MW | 10.3 | MVA | 0.22714 | 0 | 1.8 | MVA
Redmond | 115-12.5kV | 2 | 7 | Redmond | Redmond/Prineville | Deschutes | Y | N | 5D223 | 9.3 | MW | 10.3 | MVA | 0.52029 | 0 | 2.3 | MVA
Redmond | 115-12.5kV | 2 | 7 | Redmond | Redmond/Prineville | Deschutes | Y | N | 5D226 | 4.2 | MW | 10.3 | MVA | 0.10798 | 0 | 1.6 | MVA
Redmond | 115-12.5kV | 2 | 7 | Redmond | Redmond/Prineville | Deschutes | Y | N | 5D227 | 8.4 | MW | 10.3 | MVA | 0.16118 | 0 | 2.2 | MVA
Redmond | 115-12.5kV | 2 | 7 | Redmond | Redmond/Prineville | Deschutes | Y | N | 5D228 | 4.7 | MW | 10.3 | MVA | 0.0282 | 0 | 1.7 | MVA
Redmond | 115-12.5kV | 2 | 7 | Redmond | Redmond/Prineville | Deschutes | Y | N | 5D229 | 5.7 | MW | 10.3 | MVA | 0.58734 | 0 | 1.1 | MVA
Lemolo #1 | 115-12.5 kV | 1 | 1 | Roseburg | Roseburg | Douglas | N | N | 5U920 | 0.829 | MW | 1.995 | MVA | 0 | 0 | 0.29015 | MW
Myrtle Creek | 69-12.5 kV | 1 | 2 | Canyonville | Canyonville | Douglas | N | N | 5U76 | 3.65 | MW | 6.942 | MVA | 0.08189 | 0 | 1.2775 | MW
Myrtle Creek | 69-12.5 kV | 1 | 2 | Canyonville | Canyonville | Douglas | N | N | 5U77 | 6.5674 | MW | 9.166 | MVA | 0.05336 | 0 | 2.2986 | MW
Oakland | 115-12.5 kV | 1 | 2 | Oakland | Oakland | Douglas | N | N | 5U11 | 4.393 | MW | 6.505 | MVA | 0.03806 | 0 | 1.5375 | MW
Oakland | 115-12.5 kV | 1 | 2 | Oakland | Oakland | Douglas | N | N | 5U12 | 1.454 | MW | 6.505 | MVA | 0.01166 | 0 | 0.5089 | MW
Rogue River | 69-12.5 kV | 1 | 2 | Rogue River | Rogue River | Jackson | N | N | 5R77 | 6.7 | MW | 10.3 | MVA | 0.08103 | 0 | 1.2 | MW
Rogue River | 69-12.5 kV | 1 | 2 | Rogue River | Rogue River | Jackson | N | N | 5R78 | 6.3 | MW | 8 | MVA | 0.14322 | 0 | 1.5 | MW
Riddle | 115-12.5 kV | 1 | 3 | Riddle | Riddle | Douglas | Y | N | 5U1 | 5.8288 | MW | 9.353 | MVA | 0.34648 | 0 | 1.148 | MW
Riddle | 115-12.5 kV | 1 | 3 | Riddle | Riddle | Douglas | Y | N | 5U2 | 4.7841 | MW | 6.505 | MVA | 0.08199 | 0 | 1.6969 | MW
Riddle | 115-12.5 kV | 1 | 3 | Riddle | Riddle | Douglas | Y | N | 5U3 | 2.691 | MW | 6.505 | MVA | 0.0255 | 0 | 0.24199 | MW
Ross Avenue | 69-12.5 kV | 1 | 2 | Klamath Falls | Klamath Falls | Klamath | Y | N | 5L46 | 3.3 | MW | 8.04 | MVA | 0.12153 | 0 | 1.179 | MW
Ross Avenue | 69-12.5 kV | 1 | 2 | Klamath Falls | Klamath Falls | Klamath | Y | N | 5L48 | 3.6 | MW | 8.04 | MVA | 0.09516 | 0 | 1.558 | MW
Roxy Ann | 115-12.5 kV | 1 | 3 | Medford | Medford | Jackson | Y | N | 5R350 | 5.5 | MW | 10.3 | MVA | 0.23486 | 0 | 1.3 | MW
Roxy Ann | 115-12.5 kV | 1 | 3 | Medford | Medford | Jackson | Y | N | 5R354 | 8.1 | MW | 10.3 | MVA | 0.27877 | 0 | 1.6 | MW
Ruch | 69-12.5 kV | 1 | 2 | Ruch | Ruch | Jackson | N | N | 5R68 | 3.7 | MW | 7.2 | MVA | 0.3178 | 0 | 0.7 | MW
Ruch | 69-12.5 kV | 1 | 2 | Ruch | Ruch | Jackson | N | N | 5R69 | 1.9 | MW | 3.9 | MVA | 0.08212 | 0 | 0.5 | MW
Running Y | 69-20.8 kV | 1 | 1 | Klamath Falls | Klamath Falls | Klamath | N | N | 4L50 | 3.874 | MW | 9.375 | MVA | 0.11701 | 0.882 | -0.24826 | MW
Russellville | 115-12.5 kV | 2 | 4 | Portland | Portland | Multnomah | Y | N | 5P274 | 7.4 | MW | 9.5 | MVA | 0.27508 | 0 | 2.33 | MW
Russellville | 115-12.5 kV | 2 | 4 | Portland | Portland | Multnomah | Y | N | 5P276 | 7.2 | MW | 9.5 | MVA | 0.07174 | 0 | 2.059 | MW
Russellville | 115-12.5 kV | 2 | 4 | Portland | Portland | Multnomah | Y | N | 5P278 | 8.1 | MW | 10.3 | MVA | 0.24823 | 0 | 2.33 | MW
Russellville | 115-12.5 kV | 2 | 4 | Portland | Portland | Multnomah | Y | N | 5P280 | 6 | MW | 9.5 | MVA | 0.01697 | 0 | 2.18 | MW
Sage Road | 115-12.5 kV | 2 | 6 | Medford | Medford | Jackson | N | N | 5R209 | 5.6 | MW | 10.3 | MVA | 0 | 0 | 1.7 | MW
Sage Road | 115-12.5 kV | 2 | 6 | Medford | Medford | Jackson | Y | N | 5R211 | 6.7 | MW | 10.3 | MVA | 0.21539 | 0 | 1 | MW
Sage Road | 115-12.5 kV | 2 | 6 | Medford | Medford | Jackson | Y | N | 5R226 | 6.2 | MW | 9.5 | MVA | 0.05762 | 0 | 1.8 | MW
Sage Road | 115-12.5 kV | 2 | 6 | Medford | Medford | Jackson | N | N | 5R27 | 2.1 | MW | 10.3 | MVA | 0 | 0 | 0.4 | MW
Sage Road | 115-12.5 kV | 2 | 6 | Medford | Medford | Jackson | N | N | 5R28 | 8 | MW | 10.3 | MVA | 0.04295 | 0 | 1.8 | MW
Sage Road | 115-12.5 kV | 2 | 6 | Medford | Medford | Jackson | N | N | 5R29 | 4.8 | MW | 10.3 | MVA | 0.0102 | 0 | 1.2 | MW
Scenic | 115-12.5 kV | 2 | 4 | Medford | Medford | Jackson | N | N | 5R174 | 8 | MW | 10.3 | MVA | 0.08783 | 0 | 2.1 | MW
Scenic | 115-12.5 kV | 2 | 4 | Medford | Medford | Jackson | N | N | 5R180 | 7.2 | MW | 10.3 | MVA | 0.03998 | 0 | 1.7 | MW
Scenic | 115-12.5 kV | 2 | 4 | Medford | Medford | Jackson | N | N | 5R182 | 7 | MW | 10.3 | MVA | 0.29969 | 0 | 1.1 | MW
Scenic | 115-12.5 kV | 2 | 4 | Medford | Medford | Jackson | N | N | 5R184 | 10.4 | MW | 10.3 | MVA | 0.07492 | 0 | 1.3 | MW
Scio | 69-12.5kV | 1 | 1 | Lincoln City | Lincoln City | Lincoln | N | N | 5M126 | 5.21 | MW | 8 | MVA | 0.15455 | 0 | 1.8655 | MW
Seaside | 115-12.5 kV | 2 | 4 | Seaside | Seaside | Clatsop | N | N | 5A80 | 5.19 | MW | 9.6 | MVA | 0.01112 | 0 | 1.4519 | MW
Seaside | 115-12.5 kV | 2 | 4 | Seaside | Seaside | Clatsop | N | N | 5A81 | 2.5 | MW | 10.3 | MVA | 0 | 0 | 0.683 | MW
Seaside | 115-12.5 kV | 2 | 4 | Seaside | Seaside | Clatsop | N | N | 5A82 | 5 | MW | 7.2 | MVA | 0.02911 | 0 | 0.80089 | MW
Seaside | 115-12.5 kV | 2 | 4 | Seaside | Seaside | Clatsop | N | N | 5A83 | 4.4 | MW | 7.2 | MVA | 0.05102 | 0 | 0.18098 | MW
Selma | 115-12.5 kV | 1 | 1 | Selma | Selma | Josephine | N | N | 5R65 | 4.8 | MW | 10.3 | MVA | 0.10825 | 0 | 1 | MW
Shasta Way | 12-4 kV | 1 | 1 | Klamath Falls | Klamath Falls | Klamath | N | N | 7L25 | 0.638 | MW | 1.5 | MVA | 0 | 0 | 0.20615 | MW
Shevlin Park | 69-12.5kV | 1 | 3 | Bend | Bend | Deschutes | Y | N | 5D238 | 8.7 | MW | 10.3 | MVA | 0.70773 | 0 | 2.6 | MVA
Shevlin Park | 69-12.5kV | 1 | 3 | Bend | Bend | Deschutes | Y | N | 5D241 | 5.8 | MW | 10.3 | MVA | 0.1977 | 0 | 2.6 | MVA
Shevlin Park | 69-12.5kV | 1 | 3 | Bend | Bend | Deschutes | Y | N | 5D243 | 5.5 | MVA | 10.3 | MVA | 0.80621 | 0 | 1.9 | MVA
Riddle Veneer | 115-12.5 kV | 1 | 2 | Riddle | Riddle | Douglas | Y | Y | 5U23 | Redacted | MW | 12.595 | MVA | 0 | 0 | Redacted | MW
Riddle Veneer | 115-12.5 kV | 1 | 2 | Riddle | Riddle | Douglas | Y | Y | 5U50 | Redacted | MW | 9.353 | MVA | 0 | 0 | Redacted | MW
Roseburg | 115-12.5 kV | 2 | 3 | Roseburg | Roseburg | Douglas | Y | N | 4U10 | 11.2225 | MW | 15.948 | MVA | 0.2502 | 0 | 3.621 | MW
Roseburg | 115-12.5 kV | 2 | 3 | Roseburg | Roseburg | Douglas | Y | N | 4U22 | 4.6294 | MW | 15.948 | MVA | 0.2192 | 0 | 1.4882 | MW
Roseburg | 115-12.5 kV | 2 | 3 | Roseburg | Roseburg | Douglas | Y | N | 4U5 | 5.7118 | MW | 15.948 | MVA | 0.03326 | 0 | 1.9804 | MW
Sprague River | 69-12.5 kV | 1 | 1 | Sprague River | Sprague River | Klamath | N | N | 5L8 | 2.4 | MW | 3.8 | MVA | 0.00304 | 0.6 | -0.10884 | MW
Slide Creek | 115-7.2 kV | 1 | 3 | Idleyld Park | Idleyld Park | Douglas | N | N | 6U76 | 0.1039 | MW | 0.3 | MVA | 0 | 0 | 0.036365 | MW
Soda Springs | 115-7.2 kV | 1 | 1 | Idleyld Park | Idleyld Park | Douglas | N | N | 6U10 | 0.005 | MW | 0.01 | MVA | 0 | 0 | 0.00175 | MW
South Gate | 69-20.8 kV | 1 | 2 | Roseburg | Roseburg | Douglas | Y | N | 4U30 | 8.9871 | MW | 15.948 | MVA | 1.6229 | 0 | 2.0742 | MW
South Gate | 69-20.8 kV | 1 | 2 | Roseburg | Roseburg | Douglas | Y | N | 4U31 | 5.8846 | MW | 15.948 | MVA | 0.13777 | 0 | 1.605 | MW
Stayton | 69-20.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Marion | N | N | 4M19 | 11 | MW | 15.9 | MVA | 0.70444 | 0 | 2.1156 | MW
Stayton | 69-20.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Marion | N | N | 4M353 | 12.4 | MW | 21.6 | MVA | 0.45041 | 0 | 3.1496 | MW
Stayton | 69-20.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Marion | N | N | 4M370 | 6.24 | MW | 15.9 | MVA | 0.32921 | 0 | 1.4508 | MW
Stayton | 69-20.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Marion | N | N | 4M50 | 14 | MW | 21.6 | MVA | 0.38121 | 0 | 3.5288 | MW
Steamboat | 115-7.2 kV | 1 | 1 | Steamboat | Steamboat | Douglas | N | Y | 6U18 | Redacted | MW | 0.24 | MVA | 0 | 0 | Redacted | MW
Stevens Rd | 115-20.8 kV | 2 | 3 | Medford | Medford | Jackson | Y | N | 4R13 | 9.1 | MW | 16.2 | MVA | 0.05896 | 0 | 2.1 | MW
Stevens Rd | 115-20.8 kV | 2 | 3 | Medford | Medford | Jackson | Y | N | 4R17 | 8.1 | MW | 16.2 | MVA | 0.13828 | 0 | 3.4 | MW
Stevens Rd | 115-20.8 kV | 2 | 3 | Medford | Medford | Jackson | Y | N | 4R41 | 4.2 | MW | 16.2 | MVA | 0.16885 | 0 | -1 | MW
Sutherlin | 115-12.5 kV | 1 | 3 | Sutherlin | Sutherlin | Douglas | Y | N | 5U35 | 3.4842 | MW | 9.207 | MVA | 0.0056 | 0 | 1.0692 | MW
Sutherlin | 115-12.5 kV | 1 | 3 | Sutherlin | Sutherlin | Douglas | Y | N | 5U36 | 4.5573 | MW | 9.207 | MVA | 0.03394 | 0 | 1.7282 | MW
Sutherlin | 115-12.5 kV | 1 | 3 | Sutherlin | Sutherlin | Douglas | Y | N | 5U56 | 3.1152 | MW | 9.207 | MVA | 0.0228 | 0 | 0.080156 | MW
Sweet Home | 115-20.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Linn | Y | N | 4M37 | 9.63 | MW | 16.2 | MVA | 0.11032 | 0 | 2.51 | MW
Sweet Home | 115-20.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Linn | Y | N | 4M38 | 3.75 | MW | 16.2 | MVA | 0.05729 | 0 | 1.15 | MW
Sweet Home | 115-20.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Linn | N | N | 4M93 | 4.92 | MW | 16.2 | MVA | 0.03553 | 0 | 1.8445 | MW
Sweet Home | 115-20.8kV | 2 | 4 | Willamette | Albany/Corvallis/Stayton | Linn | N | N | 4M94 | 11.58 | MW | 16.2 | MVA | 4.8504 | 0 | 0 | MW
Takelma | 115-20.8 kV | 1 | 1 | Medford | Medford | Jackson | Y | N | 4R9 | 8.5 | MW | 12.5 | MVA | 0.18303 | 0 | 2.9 | MW
Talent | 115-12.5 kV | 2 | 4 | Medford | Medford | Jackson | Y | N | 5R237 | 7.6 | MW | 10.3 | MVA | 0.40208 | 0 | 2 | MW
Talent | 115-12.5 kV | 2 | 4 | Medford | Medford | Jackson | Y | N | 5R238 | 4.8 | MW | 10.3 | MVA | 0.35121 | 0 | 1.4 | MW
Talent | 115-12.5 kV | 2 | 4 | Medford | Medford | Jackson | Y | N | 5R239 | 5.5 | MW | 10.3 | MVA | 0.4066 | 3 | 1 | MW
Talent | 115-12.5 kV | 2 | 4 | Medford | Medford | Jackson | Y | N | 5R240 | 4.1 | MW | 10.3 | MVA | 0.02539 | 0 | 1.2 | MW
Texum | 69-12.5 kV | 1 | 3 | Klamath Falls | Klamath Falls | Klamath | Y | N | 5L112 | 3.29 | MW | 11.03 | MVA | 2.7595 | 0 | 0.955 | MW
Texum | 69-12.5 kV | 1 | 3 | Klamath Falls | Klamath Falls | Klamath | Y | N | 5L113 | 4.78 | MW | 11.03 | MVA | 0.03 | 0 | 1.977 | MW
Texum | 69-12.5 kV | 1 | 3 | Klamath Falls | Klamath Falls | Klamath | Y | N | 5L116 | 4.67 | MW | 11.03 | MVA | 3.0139 | 3 | -3.718 | MW
Tiller | 115-12.5 kV | 1 | 1 | Tiller | Tiller | Douglas | N | N | 5U89 | 0.625 | MW | 5.071 | MVA | 0 | 0 | 0.21875 | MW
Toketee | 115-7.2 kV | 1 | 1 | Toketee Falls | Toketee Falls | Douglas | N | Y | 6U21 | Redacted | MW | 2.514 | MVA | 0 | 0 | Redacted | MW
Toketee stepdown | 115-7.2 kV | 1 | 1 | Toketee Falls | Toketee Falls | Douglas | N | Y | 8U12 | Redacted | MW | 0.3 | MVA | 0 | 0 | Redacted | MW
Tolo | 69-12.5 kV | 1 | 3 | Medford | Medford | Jackson | N | N | 5R90 | 0.7 | MW | 3.9 | MVA | 0.02092 | 0 | 0.1 | MW
Tolo | 69-12.5 kV | 1 | 3 | Medford | Medford | Jackson | N | N | 5R91 | 4.9 | MW | 3.9 | MVA | 0.13226 | 0 | 0.2 | MW
Tolo | 69-12.5 kV | 1 | 3 | Medford | Medford | Jackson | N | N | 5R92 | No Read | MW | 8.6 | MVA | 0.13032 | 0 | 0.4 | MW
Turkey Hill | 69-12.5 kV | 1 | 2 | Malin | Malin | Klamath | N | N | 5L20 | 3.74 | MW | 8.3 | MVA | 0.18871 | 0 | 0.55469 | MW
Turkey Hill | 69-12.5 kV | 1 | 2 | Malin | Malin | Klamath | Y | N | 5L23 | 4.24 | MW | 12.5 | MVA | 10.1497 | 0 | -9.69 | MW
Pendleton | 69-.12.47 kV | 6 | 7 | Pendleton | Pendleton | Umatilla | Y | N | 5W402 | 7 | MW | 10.3 | MVA | 0.31447 | 0 | 2 | MW
Pendleton | 69-.12.47 kV | 6 | 7 | Pendleton | Pendleton | Umatilla | Y | N | 5W403 | 8 | MW | 10.3 | MVA | 0.63424 | 1.56 | 1.34 | MW
Pilot Rock | 69-.12.47 kV | 2 | 2 | Pendleton | Pendleton | Umatilla | N | Y | 5W404 | Redacted | MW | 10.3 | MVA | 0 | 0 | Redacted | MW
Pilot Rock | 69-.12.47 kV | 2 | 2 | Pendleton | Pendleton | Umatilla | N | N | 5W406 | 5.5 | MW | 7.9 | MVA | 0.02473 | 4.97 | -3.6047 | MW
Weston | 69-.12.47 kV | 1 | 2 | Pendleton | Pendleton | Umatilla | Y | N | 5W7 | 1.9 | MW | 10.3 | MVA | 0 | 0.567 | 0.233 | MW
Vernon | 115-12.5 kV | 2 | 5 | Portland | Portland | Multnomah | Y | N | 5P391 | 8.8 | MW | 10.3 | MVA | 0.3334 | 0.996 | 2.044 | MW
Vernon | 115-12.5 kV | 2 | 5 | Portland | Portland | Multnomah | Y | N | 5P392 | 5.2 | MW | 10.3 | MVA | 0.14385 | 0 | 1.369 | MW
Vernon | 115-12.5 kV | 2 | 5 | Portland | Portland | Multnomah | Y | N | 5P393 | 9.4 | MW | 10.3 | MVA | 0.43085 | 0 | 2.43 | MW
Vernon | 115-12.5 kV | 2 | 5 | Portland | Portland | Multnomah | Y | N | 5P394 | 7.1 | MW | 10.3 | MVA | 0.23937 | 0 | 1.7 | MW
Vernon | 115-12.5 kV | 2 | 5 | Portland | Portland | Multnomah | Y | N | 5P395 | 6.5 | MW | 10.3 | MVA | 0.24048 | 0 | 1.37 | MW
Vilas Road | 115-12.5 kV | 1 | 3 | Medford | Medford | Jackson | Y | N | 5R110 | 4.1 | MW | 10.3 | MVA | 10.025 | 3 | -7.7 | MW
Vilas Road | 115-12.5 kV | 1 | 3 | Medford | Medford | Jackson | Y | N | 5R146 | 8.5 | MW | 10.3 | MVA | 0.30654 | 0 | 2.3 | MW
Vilas Road | 115-12.5 kV | 1 | 3 | Medford | Medford | Jackson | Y | N | 5R305 | 7.2 | MW | 10.3 | MVA | 0 | 0 | 3.3 | MW
Village Green | 115-20.8kV | 2 | 2 | Junction City | Goshen/Village Green | Lane | N | N | 4M84 | 7.46 | MW | 11.9 | MVA | 0.30444 | 0 | -2.5644 | MW
Village Green | 115-20.8kV | 2 | 2 | Junction City | Goshen/Village Green | Lane | N | N | 4M86 | 6.7 | MW | 15.96 | MVA | 6.8448 | 0 | -3.2748 | MW
Vine Street | 69-20.8kV | 1 | 2 | Willamette | Albany/Corvallis/Stayton | Linn | N | N | 4M15 | 14.44 | MW | 19.9 | MVA | 0.2121 | 0 | 3.7879 | MW
Vine Street | 69-20.8kV | 1 | 2 | Willamette | Albany/Corvallis/Stayton | Linn | N | N | 4M16 | 14.36 | MW | 15.9 | MVA | 0.4698 | 0 | 3.4202 | MW
Weston | 69-.12.47 kV | 1 | 2 | Pendleton | Pendleton | Umatilla | Y | Y | 5W40 | Redacted | MW | 10.3 | MVA | 0 | 0 | Redacted | MW
Warm Springs | 69-20.8kV | 1 | 1 | Madras | Madras | Jefferson |  | N | 4D68 | 4.8 | MW | 12.6 | MVA | 0.35813 | 0 | 1.6 | MW
Warrenton | 115-12.5 kV | 2 | 3 | Warrenton | Warrenton | Clatsop | N | N | 5A15 | 6.8 | MW | 10.3 | MVA | 0.0112 | 0 | 6.65 | MW
Warrenton | 115-12.5 kV | 2 | 3 | Warrenton | Warrenton | Clatsop | N | N | 5A16 | 7.2 | MW | 10.3 | MVA | 0.036 | 0 | 6 | MW
Warrenton | 115-12.5 kV | 2 | 3 | Warrenton | Warrenton | Clatsop | N | N | 5A20 | 5.4 | MW | 9.6 | MVA | 0.02303 | 0 | 5 | MW
Wasco | 20.8-4 kV | 1 | 1 | Wasco | Wasco | Sherman |  | N | 7K1 | 0.508 | MW | 0.87 | MVA | 0 | 0 | 0.2 | MW
Wecome Beach | 20-4kV | 1 | 1 | Lincoln City | Lincoln City | Lincoln | N | N | 7A354 | 1.18 | MW | 2.8 | MVA | 0.01046 | 0 | 0.96954 | MW
Umapine | 69-12.47 kV | 1 | 2 | Walla Walla | Walla Walla | Umatilla | N | N | 5W105 | 6.2 | MW | 10.3 | MVA | 0 | 0 | 0.8 | MW
Umapine | 69-12.47 kV | 1 | 2 | Walla Walla | Walla Walla | Umatilla | N | N | 5W106 | 5.9 | MW | 7.2 | MVA | 0 | 0 | 1.5637 | MW
Westside | 69-12.5 kV | 2 | 6 | Klamath Falls | Klamath Falls | Klamath | N | N | 5L12 | 7.3 | MW | 8.3 | MVA | 0.00939 | 2.8 | 2.5 | MW
Westside | 69-12.5 kV | 2 | 6 | Klamath Falls | Klamath Falls | Klamath | N | N | 5L15 | 2 | MW | 8 | MVA | 0.01805 | 0 | 0.61195 | MW
Westside | 69-12.5 kV | 2 | 6 | Klamath Falls | Klamath Falls | Klamath | N | N | 5L16 | 1 | MW | 8 | MVA | 0.02538 | 0 | 0.18462 | MW
Westside | 69-12.5 kV | 2 | 6 | Klamath Falls | Klamath Falls | Klamath | N | N | 5L17 | 3 | MW | 8 | MVA | 0.05674 | 0 | 0.74826 | MW
Westside | 69-12.5 kV | 2 | 6 | Klamath Falls | Klamath Falls | Klamath | N | N | 5L18 | 3.5 | MW | 8 | MVA | 0.01196 | 0 | 1.073 | MW
Westside | 69-12.5 kV | 2 | 6 | Klamath Falls | Klamath Falls | Klamath | N | N | 5L19 | 0.8 | MW | 8 | MVA | 0.01 | 0 | 0.2525 | MW
Westside | 69-12.5 kV | 2 | 6 | Klamath Falls | Klamath Falls | Klamath | N | Y | 8L10 | Redacted | MW | 6 | MVA | 0 | 0 | Redacted | MW
Weyerhauser | 69-12kV | 2 | 1 | Klamath Falls | Klamath Falls | Klamath |  | Y | N/A | Redacted | MW | 10.3 | MVA | 0 | 0 | Redacted | MW
White City | 115-12.5 kV | 3 | 7 | Medford | White City | Jackson | N | N | 5R11 | 6.8 | MW | 9.5 | MVA | 1.2343 | 0 | 0.8 | MW
White City | 115-12.5 kV | 3 | 7 | Medford | White City | Jackson | N | N | 5R12 | 7.3 | MW | 10.3 | MVA | 0.157 | 0 | 2.1 | MW
White City | 115-12.5 kV | 3 | 7 | Medford | White City | Jackson | N | N | 5R13 | 4 | MW | 9.5 | MVA | 0 | 0 | 1.2 | MW
White City | 115-12.5 kV | 3 | 7 | Medford | White City | Jackson | N | N | 5R14 | 4.5 | MW | 10.3 | MVA | 0.0168 | 0 | 1.4 | MW
White City | 115-12.5 kV | 3 | 7 | Medford | White City | Jackson | N | N | 5R19 | No Read | MW | 10.3 | MVA | 0.11818 | 0 | 0.74 | MW
White City | 115-12.5 kV | 3 | 7 | Medford | White City | Jackson | N | N | 5R66 | 7 | MW | 9.5 | MVA | 0.01906 | 0 | 1.7 | MW
White City | 115-12.5 kV | 3 | 7 | Medford | White City | Jackson | N | N | 5R76 | 9.6 | MW | 10.3 | MVA | 0.8494 | 0 | 2.3 | MW
Winchester | 115-12.5 kV | 2 | 4 | Roseburg | Roseburg | Douglas | Y | N | 5U15 | 7.1145 | MW | 9.353 | MVA | 0.08487 | 0 | 2.5195 | MW
Winchester | 115-12.5 kV | 2 | 4 | Roseburg | Roseburg | Douglas | Y | N | 5U17 | 3.2781 | MW | 9.207 | MVA | 0.10305 | 0 | 0.7851 | MW
Winchester | 115-12.5 kV | 2 | 4 | Roseburg | Roseburg | Douglas | Y | N | 5U19 | 3.3078 | MW | 6.505 | MVA | 0.08303 | 0 | 0.8359 | MW
Winchester | 115-20.8 kV | 2 | 4 | Roseburg | Roseburg | Douglas | N | N | 4U18 | 9.2595 | MW | 16.2 | MVA | 0.12411 | 0 | 3.896 | MW
Winston | 115-12.5 kV | 1 | 2 | Winston | Winston | Douglas | N | N | 5U48 | 1.945 | MW | 6.505 | MVA | 0.0411 | 0.522 | 0.68075 | MW
Winston | 115-12.5 kV | 1 | 2 | Winston | Winston | Douglas | N | N | 5U49 | 4.006 | MW | 5.071 | MVA | 0.09142 | 0 | 1.4021 | MW
Yew Ave | 115-12.5kV | 1 | 3 | Redmond | Yew Ave | Deschutes | Y | N | 5D322 | 6.4 | MW | 10.3 | MVA | 0.22462 | 0 | 1.4 | MVA
Yew Ave | 115-12.5kV | 1 | 3 | Redmond | Yew Ave | Deschutes | Y | N | 5D323 | 4.2 | MW | 10.3 | MVA | 0.07273 | 0 | 0.8 | MVA
Yew Ave | 115-12.5kV | 1 | 3 | Redmond | Yew Ave | Deschutes | Y | N | 5D325 | 6.9 | MW | 10.3 | MVA | 0.05069 | 0 | 2.3 | MVA
Young's Bay | 115-12.5 kV | 2 | 7 | Astoria | Astoria | Clatsop | N | N | 5A202 | 6 | MW | 10.3 | MVA | 0.02751 | 0 | 1.3425 | MW
Young's Bay | 115-12.5 kV | 2 | 7 | Astoria | Astoria | Clatsop | Y | N | 5A204 | 2.2 | MW | 7.2 | MVA | 0.05156 | 0 | 0.58 | MW
Young's Bay | 115-12.5 kV | 2 | 7 | Astoria | Astoria | Clatsop | N | N | 5A205 | 3.1 | MW | 7.1 | MVA | 0.04405 | 0 | 0.69095 | MW
Young's Bay | 115-12.5 kV | 2 | 7 | Astoria | Astoria | Clatsop | N | N | 5A206 | 1.5 | MW | 7.1 | MVA | 0.0373 | 0 | 0.4527 | MW
Young's Bay | 115-12.5 kV | 2 | 7 | Astoria | Astoria | Clatsop | N | N | 5A210 | 1 | MW | 9.6 | MVA | 0.0587 | 0 | 0.2213 | MW
Young's Bay | 115-12.5 kV | 2 | 7 | Astoria | Astoria | Clatsop | Y | N | 5A211 | 1.8 | MW | 10.3 | MVA | 0.03022 | 0 | 0.756 | MW
Young's Bay | 115-12.5 kV | 2 | 7 | Astoria | Astoria | Clatsop | N | N | 5A213 | 4.4 | MW | 10.3 | MVA | 0 | 0 | 1.246 | MW
Note on K87: Adam Lint: 14 RES 105 COM 30 IND 3 IRG 1 ICU 0 PSH Total 153 CUST

## Definitions
Heading Name | Description
Substation Name | Name of the distribution substation
Voltage | High voltage winding of transformer - Low voltage winding of transformer (e.g. 115-12.5 kV)
No. of Transformers | Quantity of transformers in substation used for stepping voltage from transmission to distribution voltage
No. of Feeders | Quantity of distribution feeders served from this substation
Area | Local Pacific Power operations area that the distribution substation is located in
Load Pocket | Load pocket of distribution substation - represents area in which Pacific Power transmission facilties are largely contiguous within the pocket and bound by third-party transmission or other constraints outside the pocket.
County | Oregon County in which the distribution substation is located
Feeder SCADA | Identifies whether substation breaker has near-real-time load data transmitted to central dispatch via SCADA recording. Also a feeder where time of use metering data exists.
Customer Sensitive | A feeder is marked as Customer Sensitive and load information is redacted if the load information could be readily used to derive information about a specific customer. Examples included dedicated feeders or feeders where one customer is the signficant majority of the load served by that feeder.
Feeder Designation | Pacific Power alphanumeric circuit name
Minimum Daytime Load (MDL) | The annual minimum daytime load (MDL) from April 1, 2019 to April 1, 2020 during hours 0800-1800 measured at the substation breaker. For feeders with SCADA the minimum load will be obtained from PI ProcessBook in the timeframe specified. SCADA feeders include existing generation, but not proposed generation. For the purposes of the Oregon Community Solar program the circuits that have SCADA (those that have a ‘Y’ in column H), the eligible size should be calculated as Minimum Daytime Load (Column Q) – Proposed DER in Queue (Column P). For feeders without SCADA the minimum load will be 35% of minimum monthly peak. Non-SCADA feeders do not include existing or proposed generation. For the purposes of the Oregon Community Solar program the circuits that do not have SCADA (those that have an ‘N’ in column H), the eligible size should be calculated as Minimum Daytime Load (Column Q) – Proposed DER in Queue (Column P) – Existing DER Connected (Column O). Negative value indicates negative net load due to existing generation exceeding load.
Feeder Load Peak (Summer) | The summer peak load for the circuit measured at the substation breaker.
Feeder Capacity (Summer) | The summer rating of the first capacity limiting conductor/equipment on the feeder. This could be the substation transformer, conductor, equipment, feeder loading guideline, etc.
Existing DER Connected (MW) | Total of existing connected generation on the distribution feeder, does not include queued interconnection requests. Includes small generation and net metering for entire circuit.
Proposed DER in Queue (MW) | Total of queued interconnection requests on the distribution feeder, does not include existing generating facilities. Includes small generation only.